## Slide 1: Coagulation and Flocculation Principles - Part I (cont’d)
2025
Bruce Utne, butne@nnva.gov
John Hanchak Jr., jhanchak@nnva.gov
Newport News Waterworks

## Slide 2: Presentation Objectives
Review Definitions
Overview of Coagulation Process
Basic Chemistry
Factors Impacting Coagulation
Challenges and Corrective actions

## Slide 3: Factors Affecting Coagulation
pH
Alkalinity
Temperature
Nature of NOM
Turbidity
Pre-oxidation
Mixing

## Slide 4: Factors Affecting Coagulation
Mixing Energy Input:
Need adequate dispersion of chemical into water column
  Hydrolysis reactions occur in milliseconds
Different treatment chemicals may require extended mixing time, and varying energy input (warm water vs. cold water)
Notes: Each facility will be different, every source water will be different
Some of the above mentioned factors can be overcome with the different coagulants mentioned in the course already

## Slide 5: So How do we get chemicals into the water ?????
Force the Chemical in! PUMP IT
  Higher Pressure needed to overcome back pressure
Inject it

## Slide 6
Example of a Chemical Diffuser
Combined Filter Effluent Line
96 inch Diameter
Notes: Things to point out
  Redundancy of feed lines
  Ease of access

## Slide 7
Example cross section 3/16th inch diameter
opening will deliver3.12 gpm @ 10 psi =
187 gph
Notes: Size and diameter of line as well as orifices affects chemical dispersion
How could clogging affect chemical delivery

## Slide 8
Reference: Sweitzer, Robert J., Martin E. Flentje and F. Burton Smith, “Figure 9, Chapter IX, Basic Hydraulics, page 86, Basic Water Works Manual, American Concrete Pressure Pipe Association, 1966
Chemical Sample (Chemical)
d
Notes: Why is the highest velocity water in the middle?
Why would we want to inject chemical in the middle?

## Slide 9
Example Flash Mixing System
Dual pumped diffusion system provides flexibility and redundancy
Primary flash mix (combined)
  Coagulant, lime, chlorine, coagulant aid polymer
  Normal coagulant feed point
Secondary flash mix (each treatment train)
  Coagulant, lime, coagulant aid polymer
Designed for ultimate plant capacity
Flash Mixing System
Primary (1 unit, 72-inch pipe)
  Velocity gradient, G = 645 sec-1
  Gt = 1,000
  Horizontal, end-suction centrifugal pump: Q = 2,300 gpm at 52 ft head; 40 hp
Secondary (2 units, 54-inch pipe)
  Velocity gradient, G = 1,200 sec-1
  Gt = 1,000
  Horizontal, end-suction centrifugal pump: Q = 1,200 gpm at 38 ft. head; 15 hp
Notes: Will explain velocity gradient and Gt calculation when talk about flocculation.

## Slide 10
Counter –Current Flash Mixer

## Slide 11
Reference: American Water Works Association/American Society of Civil Engineers. Water Treatment Plant Design. 3rd ed. New York: McGraw-Hill, 1998

## Slide 13
Reference: Kawamura, Susumu. “Considerations on Improving Flocculation.” Journal AWWA 6(76):328,1976. Illustrated in American Water Works Association/American Society of Civil Engineers. Water Treatment Plant Design. 3rd ed. New York: McGraw-Hill, 1998

## Slide 14
Question: Would this location provide adequate MIXING of chemicals???
How about Dispersion???
Notes: Where should chemical be added to enhance mixing
  Ideas for enhancing mixing?
Where would dispersion be the easiest?

## Slide 15: Mixing Questions
How do we confirm chemicals have been added?
  Calibration column drawdowns
  Analyzers
  Pump performance
    Over time (trending), pump capacities

## Slide 16: SCADA Monitoring

## Slide 17: Mixing Questions
How do we confirm chemicals have been added?
  Calibration column drawdowns
  Analyzers
  Pump performance
    Over time (trending), pump capacities
  SAMPLING!!
    Perform tests to ensure the desired outcome
Notes: What kind of tests can be performed specifically with coagulation?: pH before and after, alkalinity before and after

## Slide 18
“d”
Distance = 10 – 12 ft
Notes: Ask the following questions: depending on flow from the first point to the next, would this be an adequate sampling spot ?
What would affect accurate sampling and testing? DT

## Slide 19: Test Prep:
Q: What is an advantage that coagulants such as ferric sulfate have over alum?
They are not as affected by temperature.
They work over a wider pH range.
They need very little alkalinity.
They are not affected by pre-chlorination
Answer: b. They work over a wider pH range.
Water Operator Certification Exam Prep: page 66 #51

## Slide 20: Factors Affecting Coagulation
Location & Sequence of Chemical Addition: (continued)
  Sequence of Coagulant addition will influence performance
    Alkali before or after a metal coagulant ?
    Dual coagulant approach ?
    Polymers before, simultaneously, or after ?

## Slide 21
Notes: Example of multiple injection set up
What kind of redundancy does this provide?

## Slide 22: Flocculation
Review:
  Follows the coagulation process
  Process of bringing suspended particles together to form larger, more settleable floc
  Usually takes place in a chamber or environment where agitation of the chemically coagulated water occurs
Notes: WSO Water Treatment, Grade 1 Pg. 204
Proper flocculation is needed or else optimized coagulation practices go to waste!

## Slide 23: Flocculation
Purpose:
  To create opportunity for particles to collide (and stick together) to form larger floc aggregates that are more easily removed from the water
How does it happen?
  Several different mechanisms, but we will focus on mixing (applies to particles > 1μm).
  Mixing the water increases the number and frequency of particle-particle collisions (that would otherwise occur naturally).
Notes: Flocculation mechanisms:
Perikinetic (Brownian motions)
Differential settling
Orthokinetic (mixing)  fluid shear

## Slide 24: Flocculation
Mixing requires energy input!
Number of collisions depends on:
  Mixing energy
  Detention time
  In water treatment, mixing intensity is referred to as the velocity gradient, or G-value:
  G = , units of (or sec-1)

## Slide 25: Flocculation
Key design parameter:
G t = velocity gradient x detention time (in secs)
 Number of particle collisions increases with increases in mixing intensity (G) and/or detention time (t).
However, as floc particles grow in size, they become more fragile. Intense mixing in latter stages of flocculation can break-up floc.

## Slide 26
Example Flash Mixing System
Dual pumped diffusion system provides flexibility and redundancy
Primary flash mix (combined)
  Coagulant, lime, chlorine, coagulant aid polymer
  Normal coagulant feed point
Secondary flash mix (each treatment train)
  Coagulant, lime, coagulant aid polymer
Designed for ultimate plant capacity
Flash Mixing System
Primary (1 unit, 72-inch pipe)
  Velocity gradient, G = 645 sec-1
  Gt = 1,000
  Horizontal, end-suction centrifugal pump: Q = 2,300 gpm at 52 ft head; 40 hp
Secondary (2 units, 54-inch pipe)
  Velocity gradient, G = 1,200 sec-1
  Gt = 1,000
  Horizontal, end-suction centrifugal pump: Q = 1,200 gpm at 38 ft. head; 15 hp

## Slide 27: Flocculation
12VAC5-590-871
Typical Gt values (for flocculation):
  20,000 to 200,000
  Where detention time typ. 20 to 60 minutes
    VAC requires minimum detention time of 30 minutes
  And velocity gradient typ. 35 to 70 sec-1
Multiple stages to minimize short circuiting
  VAC requires minimum of 3
  Mixing energy is reduced through each successive stage
Design with variable speed drives
  VAC requires speed range of the paddles to be 0.5 to 3.0ft/sec
Notes: VAC – Virginia Administrative Code
Knowing, understanding mixing intensity and velocity gradient is important when doing jar tests  want to simulate mixing conditions of full-scale.

## Slide 28: Flocculation
To prevent floc break-up:
Taper mixing through flocculation stages
At reduced plant flows, reduce detention time in flocculators by taking units off-line.
if mixing accomplished with a rotating blade/paddle, the tip speed in the final stage of flocculation should be between 0.9 and 1.3 ft/sec. (to limit particle shear).
Notes: Tapered flocculation: Decreasing mixing intensity through flocculation stages; Higher intensity in first stage to promote particle collisions, then lower intensity in later stages to reduce floc breakup due to shear.

## Slide 29: Flocculation
How is flocculation executed?
  Mechanical means
    Vertical mixers (impellers, paddles) walking-beam
  Hydraulic means
    Superpulsators
    Baffle walls
Notes: Next: Let’s look at some examples of flocculation

## Slide 30
Notes: Hydraulic or mechanical?

## Slide 31
Notes: Baffles at Griffith Plant, Fairfax Water
Hydraulic or mechanical

## Slide 32
Notes: Hydraulic or mechanical

## Slide 33: Flocculation Basins (Griffith WTP, Fairfax)
4 Basins @ 31.5 MGD, 3-stage
DT = 36 min at max flow
Stages 1 &2:
  Hydraulic flocculation (baffled serpentine flow)
  1st Stage G = 65 s-1 at 31.5 MGD
  2nd Stage G = 30 s-1 at 31.5 MGD
Stage 3:
  Mechanical flocculation (VS vertical hydrofoil impellers)
  6 units/basin
  Variable G = 5 to 25 s-1
Notes: Griffith- Reduction in mixing energy through each stage.

## Slide 34: Flocculation Basins
Hydraulic flocculation (two stages)
  Eliminates mixers (lower operational and maintenance costs)
  Mixing energy varies with flowrate
  Sequential flow pattern approximates plug flow.
Mechanical flocculation (one stage)
  Allows some variation in mixing energy
  Vertical hydrofoil type eliminates submerged bearings.
  6 units per basin with variable frequency drives.
Notes: What are dependent variables for both mixing types?
Pros and cons for Mechanical flocculation, hydraulic flocculation.
Detention time for each? Ability for adjustments- mechanical

## Slide 35
Baffling/Baffle Walls will add Energy/Mixing
input. Amount of Energy will be dependent
on flow and temperature.
Notes: How can we adjust the flow through the basins to adjust the mixing energy WITHOUT changing the production rate?

## Slide 36: Flocculation at Newport News (Harwood’s Mill)
4 upflow Superpulsator clarifiers
  Rated for 10 MGD apiece
Provides flocculation and clarification
  Pulse provides the flocculation process
  8 sludge collection hoppers and blowdown valves provide the clarification process
Notes: Math problem: what is the needed basin volume to have a detention time of 30 minutes

## Slide 37: Flocculation
Things to consider:
  Desired floc size:
    For direct filtration, dissolved air flotation, or membrane filtration  typically pin-head size
    For sedimentation  generally desire larger floc as settling velocity depends on particle size.
  Coagulation chemistry
    Without proper coagulation chemistry, flocculation will NOT produce desired results.
Notes: Mixing energy- too little mixing prevents colloids from impacting one another, creating the larger pin head floc aggregates, too much mixing causes floc to shear apart. Mention number of flocculation units in service, whether it helps or hinders the process to have multiple units online

## Slide 38: Test Prep:
Q: In general, the size of floc that has been found for optimal settling efficiency is _______?
Pinhead-size floc
Dime-size floc
Nickel-size floc
Quarter-size floc
Answer: a. Pinhead-size
Water Operator Certification Exam Prep: page 8, #53
Notes: Do not like this question.
8/4/23: confirmed that “a.” is correct answer according to the Exam Prep book, but still not convinced this is a good answer.

## Slide 39: Test Prep:
Q: In the flocculation basins, as the floc grow in size they become ______, so the mixing must be ______, so the floc ______.
Stronger, greater, grows larger
Stronger, greater, does not settle
Fragile, slowed, does not shear
Weaker, stopped, grows larger
Answer: c. Fragile, slowed, does not shear
Water Operator Certification Exam Prep: page 23, #159

## Slide 40: Test Prep:
Q: A cloudy appearance in the last flocculation chamber is usually caused by ______.
Excessive mixing
Not enough mixing
Too much coagulant aid
Inadequate coagulant dosage
Answer: d. Inadequate coagulant dosage
Water Operator Certification Exam Prep: page 7, #48

## Slide 41: Test Prep:
Q: How can the problem of poorly formed floc be solved?
Increase the coagulant dosage
Remove excess baffles
Use a coagulant aid
Clean the sedimentation basin to reduce short-circuiting
Answer: c. Use a coagulant aid
Water Operator Certification Exam Prep: page 7, #45

## Slide 42: Test Prep:
Q: A common mistake made in the flocculation basins is _________.
Adding the coagulant aid in the first flocculator unit
To keep too many units in service
To taper the mixing gradient too steeply
To taper the mixing gradient too gently.
Answer: b. To keep too many units in service.
Water Operator Certification Exam Prep: page 82, #163

## Slide 43: Operational Improvements / Problems Encountered
Optimizing the coagulation process is an essential part of water treatment, but there will always be problems to be solved on the operational level!
Asset management
  Condition assessments
  Equipment monitoring

## Slide 44
Problem: Low Flow conditions in pump
suction- supply line = crystallization

## Slide 45
Restriction in supply piping – reduces
delivery and reliability of coagulant
feed system.
Notes: Tested pump capacities: were fine at lower flows but began to taper off at higher flows

## Slide 46
Same 4” supply pipe with higher flow
velocities; minimal amount of crystallization

## Slide 47
Address the Problem: Suction piping
needs to be replaced w/smaller diameter
pipe – WITH No adverse impact on NPSH
(delivery) of chemical pump.

## Slide 48
Replace and Reduce Size of Supply Line
Install Pulsation Dampeners – Replaces
4” suction line (reservoir)
Re-Engineering the System

## Slide 49
Move Flow meters for easier access
(cleaning – replacement)

## Slide 50
Replace ALL solid PVC piping downstream
of flow meters to application points.
(No bends etc. to cause velocity issues)
Note – Spare line with CAM-Lock fittings
CAM-Lock Quick Connect Couplings
Spare line
Notes: Ease of access- key to quick repairs and assessing problems/situations

## Slide 51
“Nyla-Braid” clear PVC, nylon reinforced
tubing. Replaces solid PVC lines.
Notes: Nyla braid/Flexible PVC- less sharp turns needed than PVC- less areas for chemical deposits and restrictions to form. Clear = able to see function of chemical delivery system. Use at HM for problem chemcials: Lime

## Slide 52
Visual –Visual –Visual
Flow Meter Displays easily seen!
Liquid Flow seen at the Injection Point!

## Slide 53
Did WE Really Correct the Problem??
Asset Management!!
Go back to the Source – Manufacturer
Perform Bulk Storage Tank Inspections
Routine PM’s on PSV’s/PRV’s
Install Strainers – Daily/Weekly inspections
Install Chemical Flow Monitoring equipment

## Slide 54
Bulk Storage Tank Inspection
Manufacturer Quality Control

## Slide 55
Equipment PM’s

## Slide 56
Flow Meter(s)
Strainers (Clear PVC)

## Slide 57
Problems - Problems
Notes: Remove?

## Slide 59
Notes: Sample line beginning to show buildup

## Slide 61
Notes: Inside orifices becoming clogged

## Slide 62
Notes: Cannot stress enough that PM schedules are needed.
Go with the lowest hanging fruit: easy to access equipment to the more complex

## Slide 63
Design Engineer’s DO have a sense of Humor!
Bruce Utne, butne@nnva.gov
John Hanchak Jr., jhanchak@nnva.gov
Newport News Waterworks

## Slide 64: End of Presentation