## Slide 1
Water Treatment Plant Operators Short Course
Disinfection
Year 2

## Slide 2: Focus of this presentation
A general review of waterworks disinfection focusing on chlorination at Water Treatment Plants
Chemistry & concepts
Regulatory requirements
Microbial inactivation
Operational implementation

## Slide 3: Topics
Disinfection Overview
Multiple Barrier Treatment
Introduction to chlorination
Chlorine reactions
Log inactivations and removals
CT Values
More chlorine reactions

## Slide 4: Expectations
What constrains disinfection?
Significance of multiple barriers
Log inactivation & log removals
Dosage problems
Where to find info in Regulations
Speak up about unclear items
Bio-breaks as needed

## Slide 5: Topics
Disinfection Overview
Multiple Barrier Treatment
Introduction to chlorination
Chlorine reactions
Log inactivations and removals
CT Values
More chlorine reactions

## Slide 6: Public water supply disinfection practices: 100 years and counting
1902 - first continuous chlorination of municipal drinking water (Belgium)
1908 - first continuous disinfection of municipal drinking water in U.S. NaOCl
1906 WTP use Ozone (Nice, France)
1914 - “It is a matter of common knowledge nowadays that the ultraviolet rays have a strong bactericidal power.”
By 1930s – filtration plus chlorine disinfection virtually eliminates waterborne illnesses in US
Notes: Jersey City NJ
Scientific American Supplement

## Slide 7: Death rate for Typhoid Fever
United States, 1900-1960
Control of Waterborne Disease (typhoid, cholera, etc.)
Among greatest achievements of the 20th century
Water treatment technologies
Water Supply and Distribution
Wastewater treatment
Source: U.S. Centers for Disease Control and Prevention, Summary of Notifiable Diseases, 1997.
Notes: 4th greatest achievement in the 20th century – behind electrification, automobile, airplane. Wilbur Wright died of Typhoid fever in 1912, age 45. 1912 – Titanic in April. In March 1912 was the Hillsville VA courthouse shootout 5 dead, 7 wounded – 57 bullets recovered, including in the bodies

## Slide 8: Chlorination
Since the early 1900s, disinfection with chlorine has proven to be effective in preventing waterborne disease outbreaks.
What have we learned?
There are widespread differences in the susceptibility of various pathogens to chlorine disinfection
Chlorine does inactivate certain pathogens exceptionally well
Chlorine has no effect on certain pathogens

## Slide 9: Disinfection Defined
Treatment technique requirements (“Treat Techs”) targeted to specific pathogens
Treat Techs include inactivation and removal
Treat Techs establish a minimum log removal/ inactivation for specific groups of pathogens
Removal credits are awarded based on specific criteria
Disinfection can be defined as the removal and/or inactivation of pathogenic organisms in water
  Physical removal
  Inactivation by chemical oxidants or equivalent agents

## Slide 10: Primary Disinfection
Primary disinfection - an integral part of the treatment process sequence required to achieve a minimum level of inactivation of specific pathogenic organisms.
Log Inactivation required based on credited log removal
Log inactivation required may be different for each specific pathogen

## Slide 11: Secondary Disinfection
Secondary disinfection - required to maintain water quality from the distribution system entry point to all service connections by providing a disinfectant residual.
The purpose of secondary disinfection is not inactivation of a target pathogen
Purpose is to provide a safeguard against chance contamination – permeation, leaching, intrusion, regrowth, and biofilms

## Slide 12: Relative Size of Pathogens
Pencil Dot (40 µm)
Bacteria
0.2 to 20 µm
Shown 20 µm
Cryptosporidium
Oocysts (2 to 7 µm)
Viruses
(0.01 to 0.1 µm)
Giardia Cyst
(5 to 15 µm)
Notes: Membrane filtration ~ 1 micron ?

## Slide 13: Presence of Coliforms
Presence of coliform bacteria in water is an indication that the water may be contaminated by pathogenic organisms.
Presence of total coliform plus E. coli in:
  Groundwater – may be contaminated by viruses
  Surface Water – may be contaminated by protozoan cysts
    Giardia lamblia cysts
    Cryptosporidium oocysts

## Slide 14: What is Acceptable Risk of Illness from Microbiological Contamination?
Indicator organisms may indicate the adequacy of treatment i.e., filtration efficiency, by R2A HPC
BUT – Indicator organisms do not have a direct relationship to the risk of illness.
Clean Water by Mark Lechevallier and Merry Buckley, American Academy of Microbiology

## Slide 15: Absence of Coliforms
Absence of coliform bacteria is considered to be sufficient evidence that pathogens are absent and the water is safe to drink if:
  the source quality is relatively consistent, and
  treatment is appropriate to the source water quality
  a primary and secondary chlorine residual is maintained, and
  the waterworks has a good history.
Notes: What other “indirect measures”?
NTU
pH for Cl state
Direct integrity test
Statistically justifiable

## Slide 16: Groundwater & Pathogenic Protozoan Cysts
Cysts should not be a concern with a true groundwater well
Natural filtration – removes the relatively large cysts
Cysts should be trapped and retained in the strata overlying groundwater
Groundwater may contain viruses which are relatively small

## Slide 17: Soil Horizon & Natural Filtration
Soil Properties and Soil Structure
Influences pore space and water movement through the horizon
Soils act like strainers or filters, filtering & purifying water and air that flow through
Notes: Ask “Who is pulling your water from wells?’ groundwater

## Slide 18: Public Health Protection Requires Worst Case Assumptions
Must assume all surface waters and surface-influenced groundwater contain Giardia and Cryptosporidium as well as other pathogens

## Slide 19: Original SWTR* Regulated
In addition to Giardia and Viruses
There is no specific removal or inactivation criteria in the SWTR or elsewhere for Legionella or heterotrophic bacteria or pathogens in general
But they are mandated under the NPDWR to be regulated
*Surface Water Treatment Rule

## Slide 20: Safe Drinking Water Amendments & Subsequent Amendments
Provide standards for the control of specific biological contaminants:
  Giardia
  Viruses
  Cryptosporidium
Legionella, heterotrophic bacteria, and any of the many other pathogenic organisms
control of microbiological contamination in general

## Slide 21: Topics
Disinfection Overview
Multiple Barrier Treatment
Introduction to chlorination
Chlorine reactions
Log inactivations and removals
CT Values
More chlorine reactions

## Slide 22: Multiple Barrier Disinfection Approach Meets DBP and Disinfection Goals
Safeguards drinking water against most microorganisms treated by chlorine
Inactivation of chlorine-resistant protozoa, including Cryptosporidium and Giardia
Notes: Does UV provide a residual? Ozone? Peroxide?

## Slide 23: Multiple Barrier Treatment
Multiple barrier treatment is necessary in order to provide consumers with drinking water that is sufficiently free of microbial pathogens to prevent waterborne disease.
Multiple barrier treatment includes:
  Source selection
  Removal by filtration and
  Inactivation by disinfection
  Maintenance of distribution system

## Slide 24
Multiple Barrier Treatment
Focus on multiple barrier strategy to enhance overall plant performance + increase public health protection
Disinfection Barrier
Variable Quality Source Water
Coagulant Addition

## Slide 25: Multiple Barrier Treatment
Public Health Protection Requires Multiple Safeguards
Must considered the germicidal efficiency of any disinfectant for each specific pathogen which may be present
Because of the unknown
Need the Multiple Barriers of Protection for each specific pathogen which may be present

## Slide 26: Multiple Barrier Treatment
The original SWTR as implemented in Virginia required 2.5-log removal of Giardia
The remaining required 0.5-log Giardia inactivation controlled Legionella, heterotrophic bacteria, and any other pathogenic organisms present
The remaining 0.5-log Giardia cyst inactivation:
  Provided a supplement to filtration
  maintained a 2nd treatment barrier for microorganisms
Multiple barrier treatment is then provided for each targeted pathogen

## Slide 27: Topics
Disinfection Overview
Multiple Barrier Treatment
Introduction to chlorination
Chlorine reactions
Log inactivations and removals
CT Values
More chlorine reactions

## Slide 28: Chemical Oxidants/Equivalent Agents
Free Chlorine
Combined Chlorine
Ozone
Chlorine Dioxide – Hamilton! Ohio
Potassium Permanganate
UV Radiation
Ozone/Hydrogen Peroxide
Course focus is inactivation by free chlorine

## Slide 29: Chlorination to disinfect water

## Slide 30: Chlorine Disinfection
Most commonly used disinfectant
Long history of use
Germicidal efficiency established for each specific group of pathogens
Efficient inactivation conditions established
Limitations are understood

## Slide 31: Forms of Chlorine
Gas
  compressed into a liquid
  steel containers
Solid
  calcium hypochlorite powder
  “tabs” or HTHTM (& granules)
Liquid
  sodium hypochlorite solution
  industrial strength 12.5%
  household bleach 5.5%

## Slide 32: Available Chlorine
Gas, Solid (tabs), or Liquid (bleach)
Can provide same disinfection efficiency
– IF same amount of available chlorine is added
Measurement of available chlorine is reported in pounds or mg/L

## Slide 33: Dose
Dose = available chlorine added
Dose = expressed as the concentration of available chlorine added
Chlorine Concentration

## Slide 34: Chlorine Residual
Is the remaining concentration:
After a specific time period
At a given point
Chlorine concentration measured and reported as mg/L
Residual without the location is useless information
  need some idea of the contact time
  same location used as a reference

## Slide 35: Chlorine Demand
Is the amount "consumed“
  Demand = (Applied - Residual)
  Demand = (Dose - Residual)
Expressed as concentration (mg/L)

## Slide 36: Disinfection Criteria
A surface water filtration plant must provide a minimum
  3-log (99.9%) removal/inactivation of Giardia cysts
  3-log (99.9%) removal/inactivation of Cryptosporidium oocysts
  4-log (99.99%) inactivation of viruses
For each pathogen type
  Log removal credits are assigned each filtration process
  Required – removal credit = Log inactivation level required
  No removal credit for viruses

## Slide 37: Log vs Percent
Log Inactivations and Percent Inactivations
Log Inactivation | Percent Inactivation
0.0 | 0.000
0.5 | 68.38
1.0 | 90.00
2.0 | 99.00
3.0 | 99.90
4.0 | 99.99
5.0 | 99.999
6.0 | 99.9999
7.0 | 99.99999

## Slide 38: Treatment Requirements
Removal and/or Inactivation
Inactivation of those remaining after removal
Verified removal/inactivation
Multiple Treatment Barriers for each pathogen

## Slide 39: Key Indicators of Removal/Inactivation
Challenge studies
Microscopic particulate analysis
Particle counters
Laser turbidimeters
Settled water NTU
Filtered water NTU
POE NTU
REMOVAL INACTIVATION
Disinfectant dose
Contact time
Residual
pH
Temperature
Bacteriological testing

## Slide 40
Type of filtration | Maximum log removal credit for filtration |  | Minimum required log inactivation by disinfection Note 1 | 
 | Giardia | Viruses | Giardia | Viruses
Conventional | 2.5 | zero | 0.5 | 4.0
Direct | 2.0 | zero | 1.0 | 4.0
Pre-engineered package | 2.0 | zero | 1.0 | 4.0
Diatomaceous Earth | 2.0 | zero | 1.0 | 4.0
Slow Sand | 2.0 | zero | 1.0 | 4.0
Ultra or Micro Membrane | 3.0 | zero | 0.5 Note 2 | 4.0
Bag or Cartridge | 3.0 | zero | 0.5 Note 2 | 4.0
Notes: Note 1 – filtration + disinfection = min removals
Note 2 – Need 0.5 Giardia for membranes

## Slide 41: 12VAC5-590-500 TABLE 500.1
Maximum Log Removal Credits for the Various Filtration Technologies and
The Resulting Minimum Required Logs of Inactivation by Disinfection.
  Note 1 – The sum of the log removals for filtration plus the log inactivations by disinfection shall equal or exceed 3.0 for Giardia and 4.0 for viruses.
  Note 2 – Membrane filtration achieves the required 3.0 log removal of Giardia without inactivation by disinfection. However, ultra- and micro-class membranes cannot adequately remove bacterial pathogens, therefore, at least 0.5 log inactivation by disinfection is required.

## Slide 42: Chlorine Contact Time (CCT)
Time of contact or reaction
Between the point of addition and the residual measurement point
Length of time water stays in a specific unit process based on volume of the structure and flowrate in and out of the structure
Usually set by pump rates and tank volume
Sounds like Hydraulic Retention Time HRT=V/Q?
CCT generally is NOT = V/Q

## Slide 43: Chlorine Residual
Determined for both primary ands secondary disinfection
Testing in plant is for primary disinfection control
Testing in the distribution system is for secondary disinfection control
Results used for both compliance reporting and operational control monitoring
Changes with time
Location of measurement point is important
Reporting
  Trace = 0.2 mg/L Free Residual Chlorine
  <0.2 mg/L = non-detectable (out-dated, but still a good target)

## Slide 44: Topics
Disinfection Overview
Multiple Barrier Treatment
Introduction to chlorination
Chlorine reactions
Log inactivations and removals
CT Values
More chlorine reactions

## Slide 45: Chlorine Chemistry
Reactions with the three forms of chlorine
Free residual chlorine (FRC)
How pH affects inactivation efficiency
Reactions with ammonia
Combined residual chlorine (CRC)
Measuring residual chlorine

## Slide 46: Chlorine Gas
Hydrolyzes rapidly in water to form hypochlorous acid (HOCl)
The following equation presents the hydrolysis reaction:
Cl2(g) + H2O → HOCl + H++ Cl-
Chlorine gas fed to water reduces pH of the water due to production of hydrogen ion.
Hypochlorous acid also produced

## Slide 47: Calcium Hypochlorite, Ca(OCl)2
Solid “tabs” (HTHTM) & granules)
Granular calcium hypochlorite typically contains 65 percent available chlorine
Purity Equation
Dosage required = dosage desired / purity
Notes: Dosage & purity - example 50% pure?

## Slide 48: Calcium Hypochlorite, Ca(OCl)2
Formed from the precipitate that results from dissolving chlorine gas in a solution of calcium oxide (lime) and sodium hydroxide.
Tablets may not be suitable for use with potable water due to the binder used
NSF/ANSI Standard 60: Drinking Water Treatment Chemicals -- health effects standard for chemicals which are used to treat drinking water.

## Slide 49: Ca(OCl)2 Produces HOCl
The reaction between calcium hypochlorite and water is shown in the following reaction:
Ca2(OCl)2 + 2H O → 2HOCl + Ca++ + 2OH-
The application of calcium hypochlorite to water also produces hypochlorous acid
The addition of calcium hypochlorite to water yields hydroxyl ions that will increase the pH of the water.

## Slide 50: Calcium Hypochlorite, Ca(OCl)2
Solubility 1.125 lbs. per gallon
Maximum solution strength 1% or 10,000 mg/l
Tabs lose 10% strength over a year
Lime used in manufacturer may create problems with solution feed system

## Slide 51: Calcium Hypochlorite, Ca(OCl)2 Scaling
Hardness > 75 to 100 mg/L
Control scale in hypochlorinator
  Equal amounts HTH and soda ash, let settle 24 hr, decant, and use clear liquid
  Ion exchange to reduce hardness
  Sequester with 2 to 5 mg/l sodium hexametaphosphate added to make up water
Fluoridation system should include a water softener

## Slide 52: Sodium Hypochlorite Solution
Sodium hypochlorite is produced when chlorine gas is
dissolved in a sodium hydroxide solution
The reaction between sodium hypochlorite and water is shown in the following reaction:
NaOCl + H2O → HOCl + Na+ + OH-
The application of sodium hypochlorite to water produces
hypochlorous acid
Similar to chlorine gas hydrolysis
Increases the pH of the water
Clorox bleach
Notes: NOTE: NSF approved, NO additives, no “fresh smelling”

## Slide 53: Same Result all forms of Chlorine
Gas → HOCl hypochlorous acid
Ca(OCl)2 → HOCl hypochlorous acid
Bleach → HOCl hypochlorous acid

## Slide 54: HOCl Hypochlorous Acid
Weak acid that dissociates to yield
HOCl ↔ H+ + OCl-
"hypochlorous acid ↔ hydrogen ion + hypochlorite ion"
Free Available Chlorine = hypochlorous acid + hypochlorite ion
Measuring concentration of HOCl + OCl- when measure Free Residual Chlorine

## Slide 55: HOCl ↔ H+ + OCl-
-
Equilibrium Reaction
Can shift to one side or the other
One species will predominate over the other
Which way it shifts - Left or right
  Below a pH of 6.5, no dissociation of HOCl occurs
  Above a pH of 8.5, complete dissociation to OCl- occurs
Notes: pH impact

## Slide 56: pH Concept
Ionization constant for pure water at 250C Kw = [H+][OH-] = [10-7] [10-7] = 10-14
Negative logarithms of hydrogen ion concentration
pH = - log [H+]
pH scale 0 to 14
pH = 7 is absolute neutrality
Acid range 0 to <7
Alkaline range >7 to 14

## Slide 57: pH Values & Free Chlorine Species/ Disinfection Efficiency
HOCl ↔ H+ + OCl-
Low pH
  Acidic
  HOCl predominates
  Best inactivation efficiency
High pH
  Basic
  OCl- predominates
  100 X less effective as HOCl

## Slide 58
Notes: <6.5 HOCl
>8.5 OCl-

## Slide 59: Water Containing Ammonia
NH3 + HOCl → NH2Cl + H2O
"ammonia + hypochlorous acid → monochloramine + water“
NH2Cl + HOCl → NHCl2 + H2O
"monochloramine + hypochlorous acid → dichloramine + water"
NH Cl2 + HOCl → NCl3 + H2O
"dichloramine + hypochlorous acid → trichloramine + water"
Notes: Chloramination where is this used?

## Slide 60: Combined Chlorine
Chloramines
monochloramine
dichloramine
trichloramine
Total residual chlorine = chloramines + free residual chlorine
TRC = CRC + FRC
Notes: We talk about this in Level C Disinfection Byproducts control

## Slide 61
Type | Chemical Symbol | Relative Effectiveness
Hypochlorous Acid | HOCl | 1.0
Hypochlorite ion | OCl- | 1/100
Monochloramine | NH2Cl | 1/150
Dichloramine | NHCl2 | 1/80
Trichloramine | NCl3 | Volatile No estimate
Chlorine relative effectiveness
Notes: WHAT DOES THIS TELL US?

## Slide 64: Topics
Disinfection Overview
Multiple Barrier Treatment
Introduction to chlorination
Chlorine reactions
Log inactivations and removals
CT Values
More chlorine reactions

## Slide 65: Pathogen Inactivation Efficiency
Environmental effects
  pH
  Temperature
Disinfection efficiency
  Different for each pathogen
  Different for each disinfectant

## Slide 66: Optimized Inactivation
The highest levels of pathogen inactivation in the chlorine contact tank are achieved with
  high chlorine residuals
  long contact times
  high water temperature*
  good mixing
  low pH*
  low turbidity
  absence of interfering substances
*pH and temperature have the most impact on pathogen inactivation by chlorine

## Slide 67: Bacteria Inactivation
Chlorine is an extremely effective disinfectant for inactivating bacteria.
A study conducted during the 1940s indicated that HOCl is more effective than OCl- for inactivation of certain bacteria.
These results have been confirmed by several researchers
HOCl is 70 to 80 times more effective than OCl- for inactivating bacteria

## Slide 68: Virus Inactivation
Chlorine is a highly effective viricide.
Under the old/former disinfection design standard of 30 minutes contact time
Easily inactivates ≥ 4.0-log

## Slide 69: Protozoa Inactivation Giardia Cysts
The resistance of Giardia cysts is much greater than resistance of viruses and bacteria
Requirements for Giardia cysts inactivation when using chlorine have been established for various pH and temperature conditions.
Laboratory studies form basis for inactivation criteria

## Slide 70: Cryptosporidium Oocysts
Protozoa Inactivation -
Chlorine has little impact on the viability of Cryptosporidium oocysts when used at the relatively low doses encountered in water treatment (e.g., 5 mg/L).
Oocysts exposed to 80 mg/L of free chlorine for 120 minutes resulted in >3-log inactivation
Cryptosporidium oocysts inactivation with any chlorine species receives not credit

## Slide 71: Giardia Inactivation - PRIMARY
Chlorine is effective at inactivating bacteria and viruses, and Giardia cysts under established disinfection conditions
Because of chlorine’s extremely high virus inactivation efficiency, the chlorine disinfection criteria required is almost always governed by Giardia cysts inactivation.
If the required 0.5-log inactivation of Giardia for conventional filtration systems is achieved:
  then the 4-log virus inactivation will be exceeded and
  Legionella and heterotrophic bacteria and other known pathogenic organisms will be inactivated to safe levels

## Slide 72: CT Value Concept
The SWTR and amendments use the CT concept as a basis for determining inactivation efficiencies of specific microorganisms by specific disinfectants.
Efficiency or log inactivation is based on disinfection conditions of:
  contact time,
  Temperature,
  pH, and
  residual disinfectant
Notes: CT phone home. VDH-ODW and acronyms …

## Slide 73: CT phone home
Notes: 1982 – Was rejected by Columbia Pictures (having no appeal), budgeted 10.% MM grossed ~800 MM

## Slide 74: Topics
Disinfection Overview
Multiple Barrier Treatment
Introduction to chlorination
Chlorine reactions
Log inactivations and removals
CT Values
More chlorine reactions

## Slide 75: CT Value
CT represents the product of
  contact or exposure time, T, and
  the concentration of disinfectant C during the disinfection process - as measured at the end of the contact or exposure time
CT Value determines compliance with the inactivation requirements a waterworks must achieve

## Slide 76: CT Value and Corresponding Log Inactivation Varies
Depends on disinfectant used:
  Free residual chlorine
  Chloramines
  Chlorine dioxide
  Ozone
  Ultraviolet Light
Depends on target pathogen
  Giardia
  Cryptosporidium
  Viruses
  Legionella
  Heterotrophic bacteria
Notes: NSF 60 & NSF 61
1993 Milwaukee 69 dead/400,000 sick
2000 Walkerton, Ont

## Slide 77: C = Disinfectant Residual in mg/L
FRC at a specific point
After a known contact time – Actual contact time
FRC data is useless without knowing the sample point and thus some idea of the contact time
Notes: Fire hydrant testing at WCSA

## Slide 78: T = Contact Time
Mathematically expressed as
T10
(the contact time)
Estimated by multiplying:
(Hydraulic retention time) * ( baffle factor)
Measured by:
Data collected from a tracer study Tracer study much more accurate
Basin or tank T10 ≠ Hydraulic Retention Time

## Slide 79: Tracer Study
The time for a tracer to flow through a treatment unit
T10 = time at which 90 percent of the water passing through a unit is retained within that unit
T10 = time for 10 % of the dosed chemical to appear at the effluent of the unit
Notes: What causes < T10 = HRT?

## Slide 80: Chemical Tracer Study
Example:
Fluoride tracer
2.0 mg/l dose with no background fluoride
(10%) (2.0 mg/L) = 0.2 mg/L
Time for 0.2 mg/L fluoride concentration to show in the effluent = T10
Notes: Also use for max water age.
What if already fluoridating? Turn off

## Slide 81: Mathematically Estimating T10
Include hydraulic retention time in all
  Pipelines
  Tanks
  Mixing basins
  Sedimentation basins, etc.
Between the point of application and the point of residual measurement
And factors that account for the degree of short circuiting that might be expected
Notes: Example – below grade clearwell + pipe to the first tap

## Slide 82: Estimating T10
If chlorine is applied at a river intake
And the Control point is on top of the filters
The hydraulic retention time of each unit or section between application and measurement is calculated
  Raw water line
  Flash mix
  Flocculators
  Sedimentation basins
Notes: Note- with DBPs can use MnO4

## Slide 83: Estimating T10
Multiplying the theoretical contact time (hydraulic retention time) of a basin by a baffling factor that takes into account the basin’s design and probable flow pattern.
Design characteristics affect T10 values
  length-to-width ratio
  baffling within the basin
  the efficiency of inlet and outlet baffling or weirs

## Slide 84: Poor Baffling

## Slide 85: Excellent Baffling

## Slide 86: Excellent Baffling
Notes: Installed curtain

## Slide 87
Baffling Condition | Baffle Factor T10/HRT
Unbaffled (mixed flow) | 0.1
Poor | 0.3
Average | 0.5
Superior | 0.7
Perfect (plug flow) | 1.0
Baffling definitions
Notes: Plug flow – what you get credit for

## Slide 88: On the subject of baffling …
The Canterbury Tales by Geoffrey Chaucer (~1400 AD)

## Slide 89: Mathematically Estimating T10
For a tank, basin, reservoir, etc.
T10 = (HRT)(Baffle Factor)
HRT = internal volume/ peak hourly flow
  HRT = Vol / Q
Baffle Factor = T10 / HRT
T10 = (Vol / Q)(T10 / HRT)

## Slide 90: Exam Note
The formula sheet for the licensure exam only has the following:
It does not appear to have any information on baffle factors/ T10
Not sure if that means "baffle factors/ T10“ will not be on the exam, or just no equation to help you remember this.

## Slide 91: Worst Case Contact Time in a Clearwell
Worst case hydraulic retention time in a clearwell:
  Flow rate = highest (i.e., capacity)
  Water depth = lowest (after backwashing)
Conservative baffle factor
Conservative T10
Notes: AKA “most conservative”
Finished water pump shut-off

## Slide 92: 12VAC5-590-500 Tables 500.2-500.5
Log Inactivation Tables
for inactivation of Giardia cysts are based on using free chlorine at:
various water temperatures
various pHs
various FRC levels, and
T10

## Slide 93: 12VAC5-590-500 Table 500.5 Required CT Example
Free residual chlorine = 1.4 mg/L
pH = 7.5
Water temperature = 15.0 0 C
T10 = 24 min
Is the Required 0.5-log inactivation of Giardia being complied with?

## Slide 94: 12VAC5-590-500 Table 500.5 Example
Required CT for 0.5-log inactivation = 16

## Slide 95: Example continued
Operating CT = (1.4 mg/L)(24 min)
CT = 33.6 mg*min/L
Inactivation slightly over 1.0-log

## Slide 96: CT Calculations for Filtered Source
Surface water source with conventional filtration
Giardia removal credit 2.5-log
Required Giardia inactivation = 0.5 log
Chlorine added at source water pump station
First FRC operational control monitoring point is on top of the filters

## Slide 98: Calculations
Source water line 3000 ft of 8-inch diameter pipe
Source water Q = 200 gpm
FRC measured on top of filters = 0.8 mg/L
Tracer study conducted on the
– Flash mix + Flocculation + Sedimentation basins
as one unit T10 = 80 minutes
Notes: Required sed basin time?
High rate 3 hr
Rapid rate 4 hr

## Slide 99: Calculating T10 Pipeline + T10 Basins
For a pipe flowing full, T10 = HRT
Plug flow conditions prevail
Hydraulic retention time (HRT) is equal to the actual contact time = T10
HRT = Vol / Q
Volume:
HRT = gal ÷ gal/min = T10
HRT = [(0.785 D2L)(7.48gal/ft3)] ÷ gal/min

## Slide 100: Time (continued)
Time for the pipeline
1st calculate the volume
(0.785)(
8 𝑖𝑛
12 𝑖𝑛/𝑓𝑡
)2(3,000 ft)= 1,046 ft3
1,046 ft3 (7.48 𝑔𝑎𝑙)= 7,829 gal
1 𝑓𝑡3
2nd calculate the HRT
– 7,829 gal/ 200 gpm = 39 min

## Slide 101: Time (T10) Total
T10 total = T 10 pipe + T 10 basins
T10 total = 39 min + 80 min = 119 min
Actual CT
C = 0.8 mg/L T 10 total = 118.4 min
CT = (0.8 mg/L) (38.4 min + 80 min)
CT = 94.7 mg*min/L

## Slide 102: Actual Vs. Required CT
Log inactivation Achieved
At CT = 94.7 mg*min/L, 150C, and pH = 7.5
From Table 500.5
Log Inactivation achieved > 3.0-log
Log removal + log inactivation = 2.5 + 3.0 > 5.5-log

## Slide 103: When Actual Removal + Inactivation >>> Required, is it Cost Effective?
Why carry 0.8 mg/L FRC on top of the filters?
Lowering the FRC lowers the reaction kinetics and the disinfection byproducts formation potential
Can’t change the T but can change the C
Optimizing filtration efficiency has no negative public health consequences

## Slide 104: Free Residual Chlorine is lowered to 0.2 mg/L on top of the filters
Actual CT = (0.2mg/l) (118.4 min)
Actual CT = 24 mg*min/L
At 150C, pH = 7.5, and FRC = ≤0.4 mg/L
0.5-log CT = 14 mg*min/L
GOOD actual inactivation between 0.5 0.5 & 1.0-logs

## Slide 105: What Log Inactivation is Being Achieved at FCR = 0.2 mg/L
Inactivation ratio = CT actual / CT 0.5-log
Inactivation ratio = 24/14 = 1.7 Achieved log inactivation
Log inactivation = (0.5 log) (1.7) = 0.86 log
Log removal + inactivation = 2.5-log + 0.86-log = 3.36-log

## Slide 106: SW Plant Actual CT Conditions
T = 0.50C pH = 7.0
CT actual = (1.2mg/L)(20min) = 24 mg*min/L
From Table 500.3
CT 0.5-log = 33 for 0.5 log inactivation
Does not meet 0.5-log inactivation requirements
What can be changed?

## Slide 107: Adjusting CTs
Not the T10 due to
  Constant pumping rates
  Fixed CCT size
  Minimum backwash water needs
Only operational control is the chlorine dose
Increase the chlorine dose to achieve a higher FRC = higher CT

## Slide 108: Increase to What FRC?
(Cactual ) (T10 actual) = CTactual ≥ CT required
(? FRC) (20 min) = CTactual ≥ CTrequired
Required inactivation 0.5 log
0.50C and pH = 7.0
Using the same table, Table 500.2
Solve by trial and error

## Slide 109: Solving for Unknown FRC
Start at the lowest FRC listed in the Table and multiply each FRC in far-left column by the actual contact time T 10 = 20 min.
When a number ≥ the CT required for inactivation as listed in the Table is obtained, the solution is found.

## Slide 110: Operating CT Determined
Required Operating FRC
CT actual = (2.0 mg/L)(20 min) = 40 mg*min/L
CT actual ≥ CT actual required
40 mg*min/L > 39 mg*min/L
In compliance with the 0.5-log inactivation requirement

## Slide 111: Interpolating Log Inactivation
pH = 7.5
Temp = 50C
FRC = 1.0 mg/l
HRT = 90 min
Baffling factor = T10 / HRT = 0.5
T10 = HRT / T10 / HRT = (90 min)(0.5)
CT = [(1.0mg/L)] [(90min)(0.5)]
CT = 45 mg*min/L

## Slide 112: Interpolating
On Table 500.3
CT = 45 mg*min/L
Is between 0.5 and 1.0 log inactivation
Same condition of T10, pH, and FRC:
CT = 30
CT = 45
0.5 log
?.? log
CT = 60 1.0 log
0.5+[(45-30)/(60-30)] [(1.0-0.5)] = 0.75 log

## Slide 113: Interpolation Formula
X1 | Y1
X2 | Y2
X3 | Y3
30 | 0.5
45 | Y2
60 | 1.0
Y2 = [ (X2 – X1) (Y3 – Y1) ÷ (X3 – X1) ] + Y1
Solve for Y2 CT Log
Solve for Y2

## Slide 114: Know Your Log Inactivation
Base free chlorine dose and residual on the log inactivation benchmark
Adjust free chlorine residual with changes in temperature and pH
May be overdosing - prechlorine dose and/or finished water – especially in Summer
Optimize pH for disinfection
Rechlorinate in distribution system

## Slide 115: Disinfection Profile and Benchmark
Proposed changes in log inactivation should not be lowered below that which history has indicated has provided safe water.
Disinfection profile documents achieved log inactivations
Disinfection benchmark indicates the lowest inactivation achieved
Reducing the inactivation levels below the benchmark should be approached with caution

## Slide 116: Profiling and Benchmarking
Calculating the disinfection profile
  From plant records
  Giardia inactivation
Using CT value tables for the profile
Establishing the disinfection benchmark
  Daily log inactivations
  Compute monthly average over one to three years
  Lowest monthly average is the benchmark

## Slide 117: Significant Changes Requiring Approval
Moving the point of disinfectant addition
Changing the type of disinfectant
Changing the disinfection process
Making any other change designated as significant
Supporting materials for obtaining approval from the VDH-ODW must include:
  a description of the proposed change
  the disinfection profile
  an analysis of how the proposed change will affect existing levels of microbial protection.

## Slide 118: Calculating Daily Inactivation Values
Based on daily measurements of operational data
  Disinfectant residual concentration
  Contact time
  Temperature
  pH
  Peak hourly flow rate
Log inactivation plot verses time - Profile
Operating range can be readily seen

## Slide 119: Benchmark Evaluation and Approval
A minimum of 0.5-log Giardia and 4-log virus inactivation performance must be achieved at all times to comply with the VDH-ODW SWTR implementation policy and procedure
These inactivations are required to be achieved by free chlorine CT values in keeping with the multiple barrier approach to public health protection.
Inactivation levels below the benchmark may be implemented after VDH-ODW evaluation and approval.
Below the benchmark - but not below the minimums stated above

## Slide 121: Data for Profiling
Data must accurately represent the current level of disinfection
New data collection and profile if:
  Disinfection practices changed
  Plant hydraulics change
  Piping schemes changed
  Hydraulic detention time changed
Notes: Question- why would you change?

## Slide 123: Reference
Environmental Protection Agency EPA 815-R-99-013
August 1999
Disinfection Profiling and Benchmarking
Guidance Manual
http://www.epa.gov/OGWDW/mdbp/mdbptg.html#bench

## Slide 124: Topics
Disinfection Overview
Multiple Barrier Treatment
Introduction to chlorination
Chlorine reactions
Log inactivations and removals
CT Values
More chlorine reactions

## Slide 125: More Chlorine Reactions
Chloramination
Reactions with NOM
Reactions with inorganics

## Slide 126: Chlorine & Ammonia – naturally occurring Ammonia
Ammonia = Inorganic Nitrogen
NH3 + HOCl → NH2Cl + H2O
Ammonia + hypochlorous acid →
monochloramine + water
NH2Cl + HOCl → NHCl2 + H2O
monochloramine + hypochlorous acid → dichloramine + water
NH Cl2 + HOCl → NCl3 + H2O
dichloramine + hypochlorous acid → trichloramine + water

## Slide 127: Chlorine and NOM
Natural Organic Matter
  Plant and Animal Proteins
  Fecal Matter & Urine
NOM Plus Chlorine =
  Inorganic DBP
  Organic oxidation byproducts
  Halogenated Organic byproducts

## Slide 129: Chlorine and Inorganics
Hydrogen Sulfide rapid reaction, 8.5 mg/l demand
Iron and Manganese Oxidation and precipitation
  Iron at pH of 7.0
  Manganese at Ph of 10.0
Nitrites oxidized to nitrates, “blue babies”
Chlorine demand

## Slide 130: Ideal Primary Disinfectant
Employing Breakpoint Chlorination
≥ 90% FRC
≤ 10% CRC
Properties of the ideal residual
  higher oxidation potential
  more effective oxidation
  more effective disinfection
Problem - DBPs

## Slide 131: If DBPs Are a Problem
Can not totally eliminate free chlorine
Conventional filtration of surface water still only credited with 2.5 log removal of Giardia
Primary disinfection with free chlorine to achieve a 0.5 log inactivation of Giardia, Legionella, and other heterotrophic bacteria is still required
For groundwater, 4.0 log inactivation of viruses by free chlorine is required

## Slide 132: If DBPs Might be a Problem …
Thursday morning at 8:00 AM
DBP Control I
Lisa Crabtree, Deputy Field Director
Abingdon Field Office
VDH-Office of Drinking Water
It’s going to be great …

## Slide 133: Topics
Disinfection Overview
Multiple Barrier Treatment
Introduction to chlorination
Chlorine reactions
Log inactivations and removals
CT Values
More chlorine reactions

## Slide 134: For follow-up
Please contact:
David Dawson, PhD, PE
Engineering Field Office Director - Abingdon
VDH Office of Drinking Water
(276) 698-4906 (cell)
david.dawson@vdh.virginia.gov