## Slide 1: Membrane Filtration Basics
July 10, 2025
Water School
Chuck Balkenbusch
816-782-6678
cgbalkenbusch@burnsmcd.com

## Slide 2
AGENDA
Membrane History and Trends
Low Pressure Membranes
  Background
  Example Installations
High Pressure Membranes
  Background
  Example Installations
Questions
Notes: You can change this photo to be of your local Burns & Mac office. Just make sure to keep the image the same size as the sample above.

## Slide 3: A Little Background
1st Significant MF/UF System in North America in 1993 (Saratoga, CA – 3.6 mgd)
Over 500 plants now on-line for drinking water only
Historically, small facilities (i.e. < 1 mgd) for small clients
Trend is to fewer, but larger facilities
  Minneapolis – 70 mgd
  Singapore – 72 mgd
  Lancaster – 24 mgd, expandable to 36 mgd
  Lorne Park WTP, Peel ON – 100 mgd
  Lakeview WTP, Peel ON – 96 mgd
Virginia has over 20 operating membrane plants for drinking water
Limited Crypto issues and the use of UV has slowed the growth
Unattended (and reliable) operation is a major driver now

## Slide 4: Desalination Is Growing
Over 18,000 Desalination Facilities Worldwide (less than 500 in the US)
26 BGD of Total Capacity – Over 300 Million People
  0.5% of the Global Population Now
  Over 10% by 2030
Largest include:
  50 mgd in Carlsbad, CA
  28 mgd in Tampa Bay
  27 mgd in Saudi Arabia
  30 and 70 mgd in Singapore
Over 15 more planned in CA

## Slide 5: Low-Pressure Membranes

## Slide 6: What Are Low-Pressure Membranes?
Cartridge/Pressure
Submerged/Vacuum

## Slide 7: Membrane Theory Overview – Low Pressure
Colloids
Bacteria
Pollens
Yeasts
Organic macromolecules
Organic compounds
Viruses
Dissolved salts
Reverse osmosis
Nanofiltration
Microfiltration
Multimedia filter
1
0.1
0.01
0.001
0.0001
10
100 um
Hair
Visible to naked eye
Giardia
Smallest microorganisms
Polio virus
Ultrafiltration

## Slide 8: Potential Applications For Low Pressure Membranes
Turbidity/pathogen/TOC removal on raw water
Replace conventional filters following flocculation/sedimentation
Treatment of conventional filter backwash water
Pretreatment ahead of RO or NF membrane system
Fe/Mn removal following oxidation
Wastewater reuse
Arsenic removal w/ pretreatment
Pathogen removal following conventional treatment
No ability to remove PFAS/PFOA

## Slide 9: How Do Low-Pressure Membranes Work?
Membranes removes anything that is larger than its pores

## Slide 10: Pathogens of Concern
Giardia
Cryptosporidium

## Slide 11: Membrane Failure Mode
Membranes fail incrementally – one fiber at a time.
Statistically, individual fiber breaks are insignificant to the overall microbial water quality

## Slide 12: On-Line Integrity Testing
Bubble point
Air pressure
Sonic wave
Bio-challenge
Turbidity
Particle
monitoring
Direct Measures
Indirect Measures
The accepted standard is now laser turbidimeters. Detection limit  0.001 NTU.

## Slide 13: Some Key (and New) Terms
New
Permeate
Flux
Flux Decline
Specific Flux/Permeability
Reverse Filtration
Membrane Integrity
Log Removal
Recovery
Transmembrane Pressure
Old
Filtered Water
Overflow Rate
Declining Rate
Filtered Water/SF of Filter Area
Backwash
Filter Breakthrough
Filtered Turbidity
Backwash Volume
Filter Head Loss

## Slide 14: MF/UF Modes of Operation Definition
Conventional
(Dead-End)
Feed
membrane filter
Cross-flow
Feed
membrane filter
5 to 10% Recycle Flow

## Slide 15: Membrane Fouling Drives Operating Costs
Notes: 07/16/96
##
*
*

## Slide 16: Membrane Fouling Example

## Slide 17: Clean Membrane, CA 100k MWCO

## Slide 18: Dead-End Filtration – 30 Minutes

## Slide 19: Dead-End Filtration – 1 Hour

## Slide 20: NOM Layer Before Backwash

## Slide 21: NOM Layer After Backwash

## Slide 22: Coagulant Aid + NOM Before BW

## Slide 23: Coagulant Aid + NOM After BW

## Slide 24: Typical Pressure MF/UF System

## Slide 25: Submerged - Enhanced Coagulation

## Slide 26: Pressure vs. Submerged System Comparison
Pressure
Advantages
  Skid-mounted
  Easy to install
  Great for small systems
  Easy competition
  High Fluxes
Disadvantages
  Larger systems
  Fouling/energy
  Low Dosages of Coagulant
  Backwashing
Submerged
Advantages
  Use of existing tanks
  Larger systems
  Low energy
  Great for poor raw water
  Low fouling
  Backwash recovery
Disadvantages
  Modifications can be expensive
  Low flux rates
  Concentrate with fiber breakage

## Slide 27: Membrane Gravity Filtration – New Concept
Existing Air Scour Blower is used
Backwash Pump Existing is used

## Slide 28: Example Membrane Gravity Filter

## Slide 29: Filter Gallery Modifications
Air scour piping and valve relocated
Filtrate/backwash pipe added
chlorine injection added
Filtrate/backwash connection to underdrains welded closed inside pipe

## Slide 30: Cost Implications of MGF
Use of low design flux would require significant increases in membrane inventory versus “traditional” facilities
Provide low filtered water turbidity at much higher “loading rates” compared to granular media filters (i.e. more MGD per filter bed)
Membranes can be stacked to further increase capacity per filter retrofit
Capital costs for membranes further offset by significant reduction in long term operating costs:
    Longer membrane life (due to low flux)
    Less chemicals (no CIP, just low levels of BW Cl)
    Reduced operator labor costs

## Slide 31: Example Low-Pressure Membrane Plants

## Slide 32: Chesapeake, Virginia
7.5 MGD Submerged Membrane Plant
Dedicated in April 2006
Raw Water TOC – 4 to 6 mg/L
Raw Water Turbidity – 25 to 50 NTU
Coagulant Feed – 20 to 25 mg/L
Coagulant pH – 5.5 to 6.0
Membranes Replaced Due to Sand and Operation Regime
More membrane replacement than originally intended

## Slide 33: Bedford Regional Water Authority
4 MGD WTP
Direct Treatment of Smith Mountain Lake
Raw Water Turbidity - <5 NTU
Organics < 2 mg/L
No Coagulant
GAC Post-Treatment for DBP Control

## Slide 34: Lancaster, Pennsylvania Membrane Systems
24 and 12 MGD Membrane Facilities
Two of the Largest on the East Coast
Direct Treatment of Flashy Rivers with Coagulation/ Flocculation
Includes State-of-the-Art Thickening Process
Include Two-Stage Membrane Treatment with UV Disinfection
Over $70 million total cost

## Slide 35: Lancaster – Other Findings
Raw will work on flashy river water
  Need to pay attention closely during flashy events
Daily cleans – Helped when working
Heated daily cleans/backwashes helped short-term
High fluxes can be unstable
Second-stage membranes failed quicker
Clarification process is not necessarily an additional barrier or a reduction of risk
Cold water (<3oC) was difficult
Constructability and retrofit costs can be very difficult to quantify
PACl worked best in cold water
Raw water membrane costs (capital and operating) – 30 to 40% above clarified

## Slide 36: MGF Trial – Lorne Park WTP – Toronto, CA
Demonstrate reliable, stable operation at low flux, low head on a large scale
Confirm that MGF produces consistently high filtered water quality
Confirm chemical cleaning requirements
Evaluate impacts on fiber breakage
Re-use as much existing equipment as possible.
Demonstrate suitable methods/requirements of quality monitoring for MGF concept
Learn/improve in demonstration and pilot testing for advancements of the MGF concept for future implementation

## Slide 37: Key Operating Parameters
Started May 2017 and still operating until late 2018
Constant operation at 18 ML/d
Membrane backwashing every 10 hours (for 5 mins)
Low dose chlorinated backwash
No CIP
Low operating flux (< 20 L/m2/h)

## Slide 38
Chart: Date
MGF permeability (without CIP) has been stable, and mimics permeability on UF membranes (with CIP)

## Slide 39: Summary of MGF Demonstration to Date
Data to date suggests that MGF can be a sustainable process:
    Utilizing no additional energy but 3 to 4.5 feet of gravity head is required
    Re-using conventional filtration apparatus
    With dramatically reduced chemically enhanced backwash, and complete elimination of clean-in-place
  In other words, membrane quality water without the extra equipment of typical membrane filtration systems

## Slide 40: High-Pressure Membranes and Desalination

## Slide 41: Desalination Is Not New
First Commercial RO Membranes in the 1960’s
First Brackish Water RO – Ocean Reef Club, FL 1971
Improvements to RO Membranes -1970’s through 1980’s
  50% less energy usage
Membrane Softening with NF in 1977 – Pelican Bay, Naples FL
Over 20,000 plants worldwide
Largest is Ras Al Khair, Saudi Arabia: 265 mgd
  Combination of RO and thermal multistage flash (MSF) technologies
  Brought on-line in 2014

## Slide 42: Desalination 101 - Background
Issue | THEN (1900’s) | NOW (2020’s)
Cost | Cost-prohibitive | Very costly
Concentrate Disposal | Very problematic | Still a critical issue… BUT can be addressed
Need | Unnecessary | Necessary
In US municipal market, desalination means RO
Surface water RO requires significant pretreatment

## Slide 43: Other Water Cooler Desalination Tidbits
Carlsbad California is Largest US Desalination Facility (50 mgd) (Owned/operated by Poseidon)
Tampa Bay Water is Largest East Coast US Desalination Facility (28 mgd)
Ashkelon, Israel is the Largest RO Desalination In World (85 mgd)
US Lags Behind Saudi’s, UAE and Spain in contracted capacity since 2003 – Permitting Process
Majority of Construction is Design-Build (and Operate)
RO is a Commodity – Pretreatment Is Not
Virginia has “Desalination WTPs”
  Brackish Groundwater Treatment
    James City County
    Gloucester County
    Chesapeake
    Suffolk (Electrodialysis Reversal)

## Slide 44: Membrane Theory Overview – High Pressure

## Slide 45: While Alternatives Exist, RO Is Most Popular For Municipal Projects
Sea water intake and pretreatment
Reverse Osmosis (RO)
Multiple Effect Distillation
(MED / TVC / MVC)
Multi Stage Flash Evaporation (MSF)
Post treatment

## Slide 46: How Does Reverse Osmosis Work?

## Slide 47: Salt Gets Concentrated As Process Continues
FEED FLOW
Concentrated Salts
H2O
H2O
H2O
H2O
H2O
H2O
H2O
SO4
HCO3
Na
Ca
Mg
Fe
Cl
H2O
H2O
H2O
Permeate
Concentrated Salts
H2O
H2O
H2O
H2O
H2O
H2O
H2O
HCO3
Na
Ca
Mg
Ca
Cl
H2O
H2O
H2O
Permeate
SO4
FEED FLOW
Ca
Mg
Ca
Fe
Mg
Ca
SO4
SO4
Ca
SO4
Mg
Fe
SO4
Fe
H2O
H2O
H2O
Pressure

## Slide 48: What is Reverse Osmosis?

## Slide 49: Typical RO Configuration
Feed TDS (mg/L)
35,000
42,000
50,000
57,000
64,000
350
420
500
570
Osmotic P (psi)
640
906
904
903
902
Feed P (psi)
901
36% of
Total permeate
28%
20%
15%
Feed pressure = concentrate OP
+ losses + membrane resistance
Feed water

## Slide 50: Typical Seawater RO Process
High
Pressure
RO Pump
Concentrate
(To Disposal)
Lime
Carbon Dioxide
Corrosion Inhibitor
Sodium Hypochlorite
To Storage/
Distribution
J
J
2
nd
-
Pass RO
2
nd
Pass Concentrate (Recycled)
Antiscalants
Caustic Addition
1st
-
Pass RO
Chlorine Contact Basin
Energy Recovery
Cartridge
Filters
Cartridge
Filters
Raw
Seawater
from Intake
Antiscalants
MF/UF
Pretreatment
Coagulants
Shock Chlorination
Sodium Bisulfite
MF Waste
(To Disposal)
MF Filtrate
Storage
Flocculation/
Clarification
Fluoride
Aqua Ammonia
F
F
I
I
H
H
G
G
L
L
To Sludge
Handling
L
L
Notes: Bruce Long

## Slide 51: Future Trends/Considerations
Surface Water/Brackish – Pretreatment Is The Key
Chlorine Resistant Membrane
Concentrate Discharge Still An Issue
Tidal Swings Can Help
Ship-Based Desal – Real or Impractical
Alternative Energy
New Cleaning Mechanisms
Wastewater Reuse most likely for Virginia Utilities moving forward

## Slide 52: Recovery Significantly Impacts Costs
Permeate ÷ Feed Water = Recovery
Recovery Impacts Concentration Factor
Low Recovery Means:
  More feed water
  More wastewater
  More membrane area
  Lower pressures (typically)
  Less fouling (typically)

## Slide 53: Raw Water Pumping Impacts Must Be Considered
Pumping Rates of 1.5 to 2 times production rate
Intake screens
Ice
Chemical feed rates
Tidal issues
Navigation and minimum salinity levels

## Slide 54: Concentrate Discharge Will Always Be A Major Driver To Success
NPDES Permit required for Surface Water
  Industrial wastewater
  In Florida:
    “Potable water treatment by-product from desalination process”
Key Parameters of Permit
  Flow
    Daily average
    Daily maximum
  Total Dissolved Solids
    Daily average
    Daily maximum
    Single grab

## Slide 55: Mixing Zones vs. End of Pipe Limits
“Area where certain water quality criteria may be tolerable, provided this does not interfere with the existing or designated uses of the segment”
Modeling Typically Defines The Mixing Zone Boundaries

## Slide 56: Desalination Costs Are Not Low
Parameter | Brackish | Sea Water
TDS (mg/L) | 2,000 | 35,000
Equipment ($/gal) | 1.50 – 3.00 | 4.00 – 6.00
Other Installation ($/gal) | 2.00 - 3.00 | 10.00 – 16.00
Total Capital ($/gal) | 3.50 – 6.00 | 14.00 – 22.00
Est. O&M ($/kgal) | 0.50 – 0.85 | 2.50 – 3.50
Total Costs ($/kgal) | 1.50 – 2.50 | 8.00 – 12.00

## Slide 57: Typical Life-Cycle Cost Breakdown for RO
Energy is approximately 30% of total water cost
Excluding amortization cost, energy accounts for more than 50% of operating costs
Cost of Desalinated Water
Total cost: $8.00-12.00/kgal
Energy cost $0.05/kWhr; 7% interest, 25 years

## Slide 58: Example Desalination Plants

## Slide 59: Virginia Brackish Water WTPs
Chesapeake
James City County
Gloucester County
Suffolk (Electrodialysis Reversal)

## Slide 60: Tampa Bay Water Seawater Desalination Facility
Largest on the East Coast
  Drought-proof supply
  Reduce aquifer draw
  25 mgd with 6 trains (28.75 mgd all 7 trains)
1st Generation facility “flunked” 2003 acceptance test
Rebuilt pretreatment, etc. 2nd Generation facility restarted Nov 2007, now making 25 mgd

## Slide 61: Swansea, MA Desalination Facility
1.2 MGD Surface Water Desalination Facility
1.4 MGD Wellfield Project
Raw Water Pipeline
$15 million
14,000 to 20,000 mg/L TDS
Withdraw at Low-Tide
Discharge at High-Tide
End-of-Pipe Limits
3rd Place 2014 Global Award from Global Water Intelligence for Desalination Plant of the Year

## Slide 62: Greece Wind Desalination Plants – Coming to the US?
21,000 gpd
Floating and can be towed
33% Recovery
$2.8 million Euros ($3.7 million US)
  $175/gal Capital Cost!!
100% Renewable Energy

## Slide 63: Ship-Based Desalination – A New Way To Tap An Ocean Resource?
A Few Operational In Mideast
Self-Powered
  On-Board Power
  Supply From Separate Ship
Finished Water Pumped or Barged to Shore
Limited Long-Term Operating History

## Slide 64: Ship-Based vs. Land-Based Desal Comparison
Issue | Ship-Based | Land-Based
Electrical Power | Produce (AQ Issues?) | Purchase
Fuel | Power Production | None
Chemical Delivery | Trucks/Import from Shore | Trucks
Solids Handling | Bring to Shore | Traditional Systems
Pretreatment | On-shore? | Traditional Systems
Domestic Wastewater | Bring to Shore | Sewer/Septic Tank
Piloting | ?????? | Known and Understood
Permitting | ?????? | Known and Understood
Ownership/Control | ?????? | Authority-Owned/Controlled

## Slide 65: Summary
Membranes have application in drinking water treatment
Virginia is one of the most pro-low pressure membrane States in the United States
Membranes are a great particle removal mechanism
Significant fractions of organics are not normally removed with MF/UF, but when coupled with a coagulant, removals are equal to or better than conventional facilities
Desalination is growing as traditional water sources are limited and more people live along coastlines
Membranes will work on all waters, cost is just the major factor – so, pick the correct system!!!!!!