## Slide 1: Designs for Better O&M Year 3
Presented
by
Doug Hudgins

## Slide 2: Outline
Raw Water Intakes and Pumping
Pre-Sedimentation/Flocculation
Sedimentation
Filtration
Chlorine Contact Tank/Clear Well
Finished Water
SCADA
General Thoughts
Your Experience

## Slide 3: Raw Water Intake Design
Grandfathered (no or limited screening)
Screen
  Traveling vs passive
  Open size (newer permits require 1 mm)
  Cleaning
Location
  Lake
    Ability to draw from multiple levels
  River

## Slide 5: River Intake Design Considerations
New intakes in VA have a 1 mm opening requirement (approach velocity < 0.25 ft/s
  Bullet or Tee Screens
  Prone to fouling
    Algae in summer
    Leaves in fall
    Debris/turbidity during storms

## Slide 6: Bullet or Tee Screen Design
Oversize screens; assume minimum 30% blinding of the screen
Consider removable screens
Place in channel potentially with covers for algae control
Robust air burst system with water backflush
Air at screens to control frazil ice
$$ is typically the issue; ability for periods of shut down aids in reducing cost

## Slide 8: Pump Station – Raw Water
For Vertical Turbine pumps consider material upgrade from bronze due to sand/grit
Enclosed line shaft
“Standing” nickel test for vibration
Consider river level and turbidity (in addition to raw water turbidity at WTP)
Plan for pre-oxidant feed at raw water
  Access for chemical delivery

## Slide 9: Pump Station – Raw Water
Camera for viewing intake conditions/air burst
Provide remote start/stop of pumps and provide flow meter on the discharge of pumps at pump station.
Consider check valve type due to sand/grit
Pump control valves may need clean water
Sample pump needs to handle solids.

## Slide 10: Pump Station – Wet Well
Have a plan for cleaning with hatches, etc. for easy access
Submersible mixers
Jet mixing (pump and nozzles)
Water for hosing down
Partition to take one side down

## Slide 11: Pre-Sedimentation/Flocculation
Consider Static Mixers; many facilities have turned off rapid mixer
Provide ability to add chemicals before rapid/static mixer: pre-oxidant and carbon
  VDH requires carbon addition at raw water and on top of filters.
  Consider different types of PAC
Add coagulant, polymer, pH adjustment at rapid mix
Add polymer and chlorine @ last stage of flocculation

## Slide 13: Pre-Sedimentation/Flocculation
Insist on balanced hydraulics to ensure even distribution to sedimentation basins
Be able to isolate and drain all channels
For turbine style mixers, plan for tapered flocculation with speed set from control room; tied to jar testing
Parallel and series configuration
Drains in all tanks

## Slide 14: Sedimentation
Hydraulics into sedimentation basin are extremely important
Expansion to sedimentation basins are usually the worst.
Unbalanced flows will be seen in filter run times

## Slide 15: Sedimentation
Sludge withdrawal should be carefully thought out
  Sloped drainage in each way
  Mechanical withdrawal systems
  Manual removal; where is this water going?
Consider tubes/plates in existing sedimentation basins to enhance settling
High-rate processes work but must be monitored more closely due to high overflow rates

## Slide 16: Filtration
Modern filter design enables 6 gpm/ft2; VDH requires piloting above 4 gpm/ft2
Consider ability to manually & automatically backwash
Combined air/water in underdrain increases the likelihood of operation troubles

## Slide 17: Filtration
Properly sized & located air release valves on backwash lines are important
Consider replacing surface wash with air scour
Run backwash pumps against closed valve briefly to remove air

## Slide 18: Filtration
Redundant Filter?
Consider backwash recycle – green practice
Rate of flow controls – consider magmeter and modulating butterfly valve
If filtration rate is increased; headloss through filter and piping needs to be closely evaluated.

## Slide 19: CCT/Clear well
Redundant clear wells for maintenance
Design for minimum baffling factor of 0.7
Should use clear well for most of CT; minimal chlorine upstream for algae control
Finished water discharge header or other critical piping in clear well is not good practice
Provide for drains if practical or to a small pump station

## Slide 20: Finished Water
High pressure and flows can cause significant water hammer/pressure surges
  Ensure designer considers water hammer/surges
  Control valves and variable frequency drives will minimize water hammer but may not totally eliminate
  Surge tanks provide extra protection

## Slide 22: Finished Water
Add corrosion inhibitor
Corrosion test with lead coupons will help put customers at ease
Consider magmeter on discharge for flow measurement
How to control finished water pumps
  Wet well level
  Flow

## Slide 23: Chemical Feed
Peristaltic pumps that are slightly oversized have good turndown and hoses have good service life
Chemical compatibility is crucial for safety
Follow OSHA guidelines for safety showers
  Latest code requires tempered water

## Slide 24: Chemical Feed
Coriolis meters are accurate for verifying chemical flow; they require pulsation damper
Provide clear tubing at injection points to help visually verify flows
Containment is required for tanks and piping
Positive drainage is important

## Slide 27: SCADA Design Concepts
How will plant operate at startup: automatic or local start up of each equipment be required
SCADA/HMI screens: green/red : on/off or opposite
SCADA can produce monthly reports
  Export of all analog signals and daily report
  Do you want this or do you want the operator to produce these

## Slide 28: General Considerations
Equipment/pump removal
  Bridge crane
  Monorail
    Electric vs manual
  Hoists
    Electric vs manual
  Rent Crane

## Slide 30: What is your experience
Current system that is causing you fits
How would you fix it
Past problems that have been corrected
Provide feedback and examples
Email to dhudgins@chacompanies.com

## Slide 31: General Considerations
Pump/equipment layout: provide minimum 3 foot of clearance; unless additional space is required for maintenance
Large VFDs – 100 HP or larger typically require a conditioned electrical room
Consider dehumidification of piping galleries if you can afford it
Incorporate Arc Flash Study in any upgrade project.

## Slide 32: Questions