## Slide 1: Water chemistry for operators

## Slide 2: Objectives for today
Strengthen knowledge/use of water chemistry
Confidence in discussing water chemistry issues
Identify water chemistry’s elements of interest
Practice solving water chemistry problems
Provide a worthwhile use of your time
Prepare you for Short School summary test

## Slide 3: Road map for this session
General water characteristics
The Periodic Table
Key water parameters
Solutions
Chlorine disinfection
Drinking water applications
Additional exercises & questions
Note: Listings of useful formulas, terms, and conversion factors are in the ABC Formula/Conversion Table.

## Slide 4: Why do we care about water?
About 75% of the Earth’s surface is made up of water, primarily in the oceans
  Most of this water is not suitable or readily available for drinking water
Comprised solely of hydrogen and oxygen (H2O)
“Universal” solvent

## Slide 5: Water Characteristics (cont’d)

## Slide 6: Water Characteristics
Hydrophilic
  “Water loving”
  Material dissolves easily in water
Hydrophobic
  “Water hating”
  Material does not dissolve easily in water
Some compounds may have areas of each type
  Makes determining how much of a chemical will dissolve difficult

## Slide 7: Water Characteristics (cont’d)
Temperature has great effect on water
  Freezing cause hexagonal configuration and expansion – explains why freezing pipes can crack
  Boiling breaks the bonds between water molecules and allows the molecules to escape from the surface (vaporize)
The impacts of temperature on water characteristics (specific weight, density, etc.) must be taken into account in calculations

## Slide 8: Common Chemistry Units
Volume Mass
Liters (L) grams (g)
milligrams (mg)
micrograms (μg)
Milli  1 g = 1000 mg
Micro  1 g = 1,000,000 μg
Note: Abbreviations and conversion factors are located on Page 6 of the ABC Formula Sheet.

## Slide 9: Concentrations
Concentration = mass dissolved in liquid volume
1 L of Water weighs 1,000 g (Density)
*Equation on Page 4 of ABC formula sheet

## Slide 10: Concentrations
1 L of Water weighs 1,000 g (Density)
If you have 1 g of substance dissolved in 1 L of Water
1 g/L = 1 g/1,000 g = 1 part per thousand (ppt)
1 g/L = 1 ppt
If you have 1 mg of substance dissolved in 1 L of Water
1 mg/L = 1 mg/1,000 g (1 g = 1000 mg)
= 1 mg/ 1,000,000 mg = 1 part per million (ppm)
1 mg/L = 1 ppm

## Slide 11: Concentrations
1 L of Water weighs 1,000 g (Density)
If you have 1 μg of substance dissolved in 1 L of Water
1 μg/L = 1 μg/1,000 g (1 g = 1,000,000 μg)
= 1 μg/ 1,000,000,000 μg
= 1 part per billion (ppb)
1 μg/L = 1 ppb

## Slide 12: Organic Chemistry
What is organic?
  Carbon based molecules
  Carbon can have 4 bonds
Why is organic chemistry important?
  Trihalomethanes (THMs)
  Haloacetic acids (HAAs)
Reactions between Organic Carbon and Disinfectant (DBP’s)

## Slide 13: Total Organic Carbon (TOC)
Total Organic Carbon (TOC) = All organic carbon in the water
Measure TOC with a TOC Analyzer
Analyzer can also be used to measure inorganic carbon (TIC = total inorganic carbon)
  Bicarbonate and carbonate are forms of inorganic carbon
Total Carbon = TOC + TIC

## Slide 14: Inorganic Chemistry
What is inorganic chemistry?
Salts, name a few…
Sodium (Na+1), Magnesium (Mg+2), Calcium (Ca+2)
Chlorides (Cl-1), Sulfate (SO4-2),
Carbonate (CO3-2)
Notes: Difference between Chlorine and Chloride: Chlorine refers to a halogen element of the periodic table. Chloride is formed from chlorine. It can either mean any compound with chlorine in it, or specifically a salt of hydrochloric acid consisting of two elements, one of which is chlorine. An example of a chloride is sodium chloride (salt).

## Slide 15: Water & pH
H2O(L)  H+ + OH-
pH = -log10 [H+]
      pH 7 = neutral
      pH < 7 = ?
      pH > 7 = ?

## Slide 16: Water & pH
H2O(L)  H+ + OH-
pH = -log10 [H+]
pH 7 = neutral
pH < 7 = ?
pH > 7 = ?

## Slide 17: Specific Gravity
Common property of compounds that is related to density and specific weight
SG = γc/γw = ρc/ρw
where: SG = specific gravity
γc = specific weight of compound (lb/ft3)
γw = specific weight of water (lb/ft3)
ρc = density of compound (g/cm3)
ρw = density of water (g/cm3)

## Slide 18: Specific Gravity and Density
Specific gravity (SG) = ratio of density of substance to density of water (at reference temperature-usually 4 °C)
Water at 4 °C has a density of:
  SI Units: 1 g/cm3 or 1 kg/L
  English Units: 62.4 lbs/ft3 or 8.34 lbs/gal
Thus, substance with SG of 2 has a density of 2 g/cm3
SG of mercury is 13.6
* Equation on Page 4 of ABC formula sheet

## Slide 19: Specific Gravity and Density
The density of the liquid alum is 11.14 lbs/gal. Water has a density of 8.34 lbs/gal at 4 C. What is the SG of the liquid alum?
  = 1.34
Notes:   11.14/8.34 = 1.34
  𝑆𝐺= (𝑆𝑝𝑒𝑐𝑖𝑓𝑖𝑐 𝑊𝑒𝑖𝑔ℎ𝑡 𝑜𝑓 𝑆𝑢𝑏𝑠𝑡𝑎𝑛𝑐𝑒, 𝑙𝑏/𝑔𝑎𝑙)/(𝐷𝑒𝑛𝑠𝑖𝑡𝑦 𝑜𝑓 𝑊𝑎𝑡𝑒𝑟, 𝑙𝑏/𝑔𝑎𝑙)
  11.14/8.34 = 1.34

## Slide 20: Molecular Weight
Represents the total weight of a molecule
Calculated by adding up all of the weights of the individual atoms included in the molecule
  Atomic weights can be obtained from periodic table

## Slide 21: Calculating Molecular Weight
Example: Calculate the molecular weight of alum, Al2(SO4)3·14.3H2O
  Step 1: Calculate the atomic weights for all components
  2 Al = 2 x 26.98 = 53.96
  3 S = 3 x 32.06 = 96.18
  12 O = 12 x 16 = 192
  28.6 H = 28.6 x 1 = 28.6
  14.3 O = 14.3 x 16 = 228.8
  Step 2: Add results from step 1
  53.96 + 96.18 + 192 + 28.6 + 228.8 = 599.54 ≈ 600

## Slide 22: Fingertip facts
7.48 gal/ft3 – volume (ft3) of water
8.34 #/gal – weight of water
62.4 #/ft3 – density of water
1 gm/mL – weight of water
8.34 #/MG/mg/L – the “Pound Formula”

## Slide 23: Road map for this session
General water characteristics
The Periodic Table
Key water parameters
Solutions
Chlorine disinfection
Drinking water applications
Additional exercises & questions

## Slide 24: Periodic Table of the Elements

## Slide 25: Example – Periodic Table element

## Slide 26: Example – Periodic Table element

## Slide 27: Important elements …
H He
Li Be C N O F
Na Mg Al Si P S Cl
K Ca (Mn Fe Cu Zn)
Pb
Notes: 22 of 118

## Slide 28: Periodic Table footnote

## Slide 29: Road map for this session
General water characteristics
The Periodic Table
Key water parameters
Solutions
Chlorine disinfection
Drinking water applications
Additional exercises & questions

## Slide 30: Hardness
Soluble multi-charged salts (≥ +2 charge)
Expressed as calcium carbonate (CaCO3)
What is the most common causer of hardness?
  Calcium and Magnesium
Notes: Compounds of Calcium and Magnesium (Ca2+)
General guidelines for classification of waters are: 0 to 60 mg/L (milligrams per liter) as calcium carbonate is classified as soft; 61 to 120 mg/L as moderately hard; 121 to 180 mg/L as hard; and more than 180 mg/L as very hard

## Slide 31: Alkalinity
  Definition: A water’s ability to consume or neutralize acid i.e, the buffering capacity of water
  Alkalinity = [OH-] + [HCO3-] + 2[CO3-2] – [H+]
Hydroxide
Bicarbonate
Carbonate
Most Common Form of Alkalinity for Most Waters
Notes: Bicarbonate is most common; Predominates below pH 8.3

## Slide 32: Alkalinity
  Typical expressed as mg/L as CaCO3
  Alkalinity as CaCO3:
  = 100 g/mole
  = 2 eq charge/mole
  = 50 g/eq: (100 g/2 eq charge)
  = 50 mg/meq

## Slide 33: Alkalinity
Important in Coagulation  Coagulants like Alum are acidic
  ↳ Alum consume Alkalinity
Note: Alkalinity decreases by 0.5 mg/L (as CaCO3) per mg/L alum

## Slide 34: Example 3 – Alkalinity Needed
How much “hydrated lime” is needed to provide the required alkalinity under the following conditions?
Parameter | Value
Optimum alum dose, mg/L | 35
Raw water alkalinity, mg/L as CaCO3 | 20
Required settled water alkalinity, mg/L as CaCO3 | 40
Hydrated lime, Ca(OH)2 | 90% pure
Notes: 1 mg/L alum will consume 0.5 mg/L of alkalinity
Therefore, 2.5 mg/L of alkalinity will remain after alum coagulation:
20 mg/L Alkalinity Originally – 17.5 mg/L Alkalinity Consumed = 2.5 mg/L Remaining
(Remaining Alkalinity = 2.5 mg/L expressed as CaCO3 )
Want, 40 mg/L of alkalinity at the end, so need to add 37.5 mg/L of Alkalinity:
40 mg/L Alkalinity Desired– 2.5 mg/L Alkalinity Remaining = 37.5 mg/L to Be Added
Need to Add 37.5 mg/L of Alkalinity
Add the Alkalinity with Hydrated Lime (Ca(OH)2)
Lots of different Units, so multiple unit conversions are necessary
Alk as mg/L CaCO3  Hyd. Lime as mg/L lime
= 27.75 mg/L Ca(OH)2
Since the hydrated lime is 90% pure, divide by 0.90
1 mg/L alum will consume 0.5 mg/L of alkalinity
(35 𝑚𝑔 𝑎𝑙𝑢𝑚)/𝐿 𝑥 (0.5 𝑚𝑔 𝑎𝑙𝑘)/(1 𝑚𝑔 𝑎𝑙𝑢𝑚)=17.5 𝑚𝑔/𝐿 𝐴𝑙𝑘𝑎𝑙𝑖𝑛𝑖𝑡𝑦 𝐶𝑜𝑛𝑠𝑢𝑚𝑒𝑑
Therefore, 2.5 mg/L of alkalinity will remain after alum coagulation:
20 mg/L Alkalinity Originally – 17.5 mg/L Alkalinity Consumed = 2.5 mg/L Remaining
(Remaining Alkalinity = 2.5 mg/L expressed as CaCO3 )
Want, 40 mg/L of alkalinity at the end, so need to add 37.5 mg/L of Alkalinity:
40 mg/L Alkalinity Desired– 2.5 mg/L Alkalinity Remaining = 37.5 mg/L to Be Added
Need to Add 37.5 mg/L of Alkalinity
Add the Alkalinity with Hydrated Lime (Ca(OH)2)
Lots of different Units, so multiple unit conversions are necessary
Alk as mg/L CaCO3  Hyd. Lime as mg/L lime
(37.5 𝑚𝑔 𝑎𝑠 𝐶𝑎𝐶𝑂_3)/𝐿 𝑥 𝑚𝑒𝑞/(50 𝑚𝑔 𝐶𝑎𝐶𝑂_3 )=0.75 𝑚𝑒𝑞/𝐿 𝑡𝑜 𝑏𝑒 𝑎𝑑𝑑𝑒𝑑
(0.75 𝑚𝑒𝑞)/𝐿 𝑥 (1 𝑚𝑚𝑜𝑙𝑒 𝐶𝑎(𝑂〖𝐻)〗_2)/(2 𝑚𝑒𝑞) 𝑥 (74 𝑚𝑔)/(1 𝑚𝑚𝑜𝑙𝑒 𝐶𝑎(𝑂〖𝐻)〗_2 )=
= 27.75 mg/L Ca(OH)2
Since the hydrated lime is 90% pure, divide by 0.90
(27.75 𝑚𝑔)/𝐿 𝑥 1/(90%)=30.8 𝑚𝑔/𝐿 𝐶𝑎(𝑂𝐻)_2 𝑡𝑜 𝑏𝑒 𝐴𝑑𝑑𝑒𝑑

## Slide 35: Question: How much hydrated lime would you add to increase the alkalinity of a water by 55 mg/L?
=

## Slide 36: How much “hydrated lime” is needed to provide the required alkalinity under the following conditions?
1 mg/L alum will consume 0.5 mg/L of alkalinity
Therefore, 2.5 mg/L of alkalinity will remain after alum coagulation:
20 mg/L Alkalinity Originally – 17.5 mg/L Alkalinity Consumed = 2.5 mg/L remaining expressed as CaCO3
We want 40 mg/L of alkalinity at the end, so need to add 37.5 mg/L of Alkalinity:
40 mg/L Alkalinity desired– 2.5 mg/L Alkalinity remaining = 37.5 mg/L to be added
Parameter | Value
Optimum alum dose, mg/L | 35
Raw water alkalinity, mg/L as CaCO3 | 20
Required settled water alkalinity, mg/L as CaCO3 | 40
Hydrated lime, Ca(OH)2 | 90% pure

## Slide 37: How much “hydrated lime” is needed to provide the required alkalinity under the following conditions?
Need to add 37.5 mg/L of Alkalinity
Add the Alkalinity with Hydrated Lime (Ca(OH)2)
Alk as mg/L CaCO3  Hyd. Lime as mg/L lime
= 27.75 mg/L Ca(OH)2
Since the hydrated lime is 90% pure, divide by 0.90
Parameter | Value
Optimum alum dose, mg/L | 35
Raw water alkalinity, mg/L as CaCO3 | 20
Required settled water alkalinity, mg/L as CaCO3 | 40
Hydrated lime, Ca(OH)2 | 90% pure

## Slide 38: Chemical purity
Important because many common water treatment chemicals include impurities that must be accounted for
Purity ratings are provided by NSF and all chemicals used in water treatment must be NSF approved

## Slide 39: Chemical dosing - example
Assume you need to add fluoride to the water to obtain a 1 mg/L residual
Fluoride can be dosed as a sodium fluoride powder; this powder is 90-98% pure
  Assume 90% purity for this example

## Slide 40: Chemical dosing – example (cont’d)
Step 1: Calculate the percent fluoride
  %F = (At. Wt. of F / MW of NaF) * 100
  %F = (19/42)*100 = 45.2% ≈ 45%
Step 2: Determine dosing of NaF to obtain 1mg/L F
  mg/L NaF = (desired concentration) )
  (percent compound as decimal)(purity as decimal)
  = ( (1 mg/L) )
  (0.45)(0.90)
  = 2.47 mg/L NaF required to obtain 1 mg/L F residual

## Slide 41: The density of the liquid alum is 11.14 lbs/gal. Water has a density of 8.34 lbs/gal at 4 C. What is the SG of the liquid alum?
  = 1.34

## Slide 42: Liquid and Solid Alum Additions
If you need to add 500 lbs of dry alum per day to treat your water, how many lbs of liquid alum (contains 48.5% dry alum) should you add to get the same treatment?
500lbs / 0.485 = 1031 lbs/day
Notes: 500/0.485 = 1031 lbs/day

## Slide 43: Alum example
To add 1,031 lbs/day of liquid alum (48.5% dry alum), how many gal/day of liquid alum would you need to add? (Density of Alum = 11.14 lbs/gal)
1,031 lbs/day x 1 gal/11.14 lbs = 92.5 gal/day
At 2 MGD flow, how many mg/L are you adding of alum?
  Alum mg/L x 8.34 lbs/MG/mg/L x 2 MGD = 500 lbs/day
  Alum, mg/L = 500/(8.34x2) = 30 mg/L
Notes: 1,031 lbs/day x 1 gal/11.14 lbs = 92.5 gal/day
  Y mg/L x 8.34 lbs/MG/mg/L x 2 MGD = 500 lbs/day
  Y, mg/L = 500/(8.34x2) = 30 mg/L
  What is Y?

## Slide 44: The “Pound” Formula
Developed to help us convert units of dosage between metric and English units
lb/MG = 8.34 * concentration (in mg/L)
lb/day = 8.34 * conc. (in mg/L) * Q (in MGD)
Example: How many lbs/day of chemical must be added to maintain 10mg/L at a flow of 5MGD?
  lb/day = 8.34(10mg/L)(5MGD) = 417 lb/day

## Slide 45: Chemical dosing – example 2
What if the water in the previous example already contained 0.3 mg/L F ?
  Dosing = (D-E)/(F)(P)
    where D = desired concentration in the water
    E = existing concentration in the water
    F = % compound in the chemical as a decimal
    P = purity of the chemical as a decimal
NaF dose = (1 mg/L – 0.3 mg/L) / (0.45)(0.90)
= 1.73 mg/L NaF would be required

## Slide 46: Road map for this session
General water characteristics
The Periodic Table
Key water parameters
Solutions
Chlorine disinfection
Drinking water applications
Additional exercises & questions

## Slide 47: Solutions
Homogeneous mixture of two or more components
Dissolving agent is the solvent; substance dissolved is the solute
Components of a solution are atoms, ions, or molecules
Commonly use molarity and normality to define strength of the solution (Concentrations)

## Slide 48: Chemical solutions
Water can dissolve a variety of compounds
  There is a saturation point for each solution – point where no more compound will dissolve
A solvent (e.g., water) dissolves solutes (e.g., salts)

## Slide 49: Percent solution
Also called “percent concentration”
Expresses the strength of the solution
Percent solution =
(mass solute/mass solution) * 100%

## Slide 50: Percent solution - example
If 10 g solute are added to 90 g water, what is the percent solution?
% solution = ( 10 ) * 100%
(10+90)
= 10%
1% solution = 10,000 mL

## Slide 51: Molarity (M)
Expresses strength of solution in moles per liter
Moles = g of compound / molecular wt of compound

## Slide 52: Solution Concentration: Molarity
1 mole/L = 1 M solution; 2 moles/L = 2 M
Example:
What is the concentration of a 1 M solution of hydrated lime?
*Equation on Page 4 of ABC formula sheet
Notes: MW Ca(OH)2 = MW Ca + 2*(MW O) + 2(MW H)
MW Ca(OH)2 = 40.078 g/mole + 2*(15.9994g/mole)+ 2(1.00794 g/mole)
MW Ca(OH)2 = 74.093 g/mole
Thus, 1 M solution of hydrated lime = 74 g/L

## Slide 53: What is the concentration of a 1 M solution of hydrated lime?
MW Ca(OH)2 = MW Ca + 2*(MW O) + 2(MW H)
MW Ca(OH)2 = 40.078 g/mole + 2*(15.9994g/mole)+ 2(1.00794 g/mole)
MW Ca(OH)2 = 74.093 g/mole
1 M = 1 mole/L
Concentration of 1 M solution of hydrated lime = 74 g/L

## Slide 54: Example - Molarity
Example: How much NaOH in grams (g) would you put in a flask to make 1 L of a 0.1 M solution?
  MW of NaOH = 23 + 16 + 1 = 40 g/mole
  0.1 M = 0.1 moles/L, you would need…
If making a 2 L of 0.1 M solution  add 4 x 2 = 8 g NaOH
Notes:   MW of NaOH = 23 + 16 + 1 = 40 g/mole
  0.1 M = 0.1 moles/L, you would need…
If making a 2 L of 0.1 M solution  add 4 x 2 = 8 g NaOH
  MW of NaOH = 23 + 16 + 1 = 40 g/mole
  0.1 M = 0.1 moles/L, you would need…
(0.1 𝑚𝑜𝑙𝑒𝑠)/𝐿 𝑥 (40 𝑔 𝑁𝑎𝑂𝐻)/(1 𝑚𝑜𝑙𝑒)=4.0 (𝑔 𝑁𝑎𝑂𝐻)/𝐿
(4 𝑔 𝑁𝑎𝑂𝐻)/(1 𝐿) 𝑥 1 𝐿= 4 𝑔 𝑁𝑎𝑂𝐻
If making a 2 L of 0.1 M solution  add 4 x 2 = 8 g NaOH

## Slide 55: Molarity - example
How many grams of H2SO4 would be required to make a 2 M solution of H2SO4?
  MW of H2SO4 = 98 g
  Molarity = moles/1 L
  = (g H2SO4 / MW H2SO4) / 1 L
  2 M = (g H2SO4 / 98 g)/1 L
  (2 M)(1 L)(98 g) = g H2SO4
  196 g H2SO4 would be required

## Slide 56: Normality (N)
Expresses strength of solution
Refers to the number of gram equivalent weights per liter
Gram equivalent weights ~ GEW or “equivalent weights”
GEW = Molecular weight / (number of equivalents)
EXAMPLE
In H2SO4 there are 2 H+ that can be donated, so
GEW = 98 g/ 2 equivalents
= 49 g / equivalent

## Slide 57: A normal day in the lab?

## Slide 58: Solution Concentration: Normality
Na+, H+, OH-, K+, Cl-, HCO3-  1 eq/mole
Ca2+, Mg+2, CO3-2, CaCl2  2 eq/mole
Al3+, Al(OH)3  3 eq/mole
*Equation on Page 4 of ABC formula sheet

## Slide 59: Normality question
If you dilute 4 g of Ca(HCO3)2 to 1 L with water, what is the normality of the 1 L solution?
Note: Ca(HCO3)2 : MW = 162 g/mole; 2 eq/mole
Notes: (4 𝑔 𝐶𝑎〖(𝐻𝐶𝑂_3)〗_2)/(1 𝐿) 𝑥 (1 𝑚𝑜𝑙𝑒 𝐶𝑎〖(𝐻𝐶𝑂_3)〗_2)/(162 𝑔 𝐶𝑎〖(𝐻𝐶𝑂_3)〗_2 ) 𝑥 (2 𝑒𝑞)/(1 𝑚𝑜𝑙𝑒)=0.05 𝑒𝑞/𝐿=0.05 𝑁

## Slide 60: Normality - example
How much NaOH is required to make a 2N solution?
MW of NaOH = 40 g
NaOH only has 1 OH- to donate
GEW = 40 g / 1equivalent = 40 g
1N = GEW / 1L = 40g/L
so to make 2N solution
= 40 g/L * 2
= 80 g/L NaOH

## Slide 61: Normality (cont’d)
In most cases, GEW is equal to the MW of a compound divided by the charge on the cation or anion
  Example: CaCO3
  MW = 100 g; Ca = +2 charge, CO3 = -2 charge
  GEW = 100 / 2 = 50 g/equivalent

## Slide 62: Normality example 2
Normality commonly used for titrations, dilutions, etc.
N1V1 = N2V2
Example (dilution): How much of a 36N solution would be needed to make 1L of a 6N solution?
N1V1 = N2V2
(36N)(V1) = (6N)(1L)
V1 = 0.167 L
= 167 mL

## Slide 63: Normality example 3
Example (titration): A sample has 80 mg/L as CaCO3 alkalinity. How many mL of 0.02N H2SO4 would be required to titrate 50 mL of the sample?
  For CaCO3, the GEW is 50 g/equivalent (50 mg/meq)
  (80mg/L) / (50mg/meq) = 1.6 meq/L
  = 0.0016 eq/L
  = 0.0016N CaCO3
  N1V1 = N2V2
  (0.0016N CaCO3)(50mL) = (0.02N H2SO4)(V2)
  4mL H2SO4 would be required

## Slide 64: Road map for this session
General water characteristics
The Periodic Table
Key water parameters
Solutions
Chlorine disinfection
Drinking water applications
Additional exercises & questions

## Slide 65: Chlorine Disinfection
Chlorination Mechanics:
Chlorine gas added to water
Cl2(g) + H2O  HOCl + H+ + Cl-
HOCl  H+ + OCl-
Free Chlorine: [Cl2] + [HOCl] + [OCl-]
Total Chlorine: Free Chlorine + Reactive Chlorine Bound with other Entities like Ammonia

## Slide 66: Chlorine Disinfection
HOCl  H+ + OCl-
Increase pH  More OCl-
Decrease pH  More HOCl

## Slide 67: Chlorine Disinfection
HOCl is about 80 – 200 stronger disinfectant than OCl- ! ! !

## Slide 68: Chlorine reactions (1 of 2)

## Slide 69: Chlorine reactions (2 of 2)

## Slide 70: Disinfection Byproducts
Covered in separate sessions this week

## Slide 71: Road map for this session
General water characteristics
The Periodic Table
Key water parameters
Solutions
Chlorine disinfection
Drinking water applications
Additional exercises & questions

## Slide 72: Drinking water applications
The Pound Formula
Taste & Odor
Copper & Copper Sulfate
Iron & Manganese

## Slide 73: The “Pound” Formula
Developed to help us convert units of dosage between metric and English units
lb/MG = 8.34 * concentration (in mg/L)
lb/day = 8.34 * conc. (in mg/L) * Q (in MGD)
Example: How many lbs/day of chemical must be added to maintain 10mg/L at a flow of 5MGD?
  lb/day = 8.34(10mg/L)(5MGD) = 417 lb/day

## Slide 74: Taste and Odor
Earthy and musty T&O generally due to geosmin and 2-methyl-isoborneol (MIB)
Attributed to cyanobacteria (blue-green algae), actinomycetes (higher bacteria; especially streptomyces), and fungi
Organisms develop in summer and early fall

## Slide 75: Geosmin
IUPAC…4,8a-dimethyldecalin-4a-ol
Other name…Octahydro-4,8a-dimethyl-4a(2H)-naphthalenol
C12H22O
Molar mass 182.3 g/mol
CAS number 19700-21-1
Literal translation “earth smell”
Odor characterized as “earthy”
or “muddy”

## Slide 76: 2-Methylisoborneol (MIB)
IUPAC…1,6,7,7-Tetramethylbicyclo[2.2.1]heptan-6-ol
Other name…2-Methyl-2-bornanol
C11H20O
Molar mass 168.28 g/mol
CAS number 2371-42-8
Odor characterized as “musty”

## Slide 77: Taste and Odor Control
Oxidation
  Chlorine
  Potassium permanganate
  Ozone
  Chlorine dioxide
Adsorption
  Use of sorbent; e.g., carbon
Aeration
  volatility

## Slide 78: T&O Control with Chlorine
Cl2, HOCl, OCl-1
Low level odors
May increase odors; e.g., if caused by MIB
Disinfection by-products (DBPs) might form

## Slide 79: T&O Control with Potassium Permanganate
KMnO4
Often effective for algae and industrial odors
Effective at higher pH
Dose… 1-3 mg/L
Contact time… 1-2 hrs
Be careful not to overdose

## Slide 80: T&O Control with Ozone
O3
Strongest oxidant
Dose… 0.5-5.0 mg/L
Not always successful
Bromates (a DBP) might form
Generated on-site
Cost

## Slide 81: T&O Control with Chlorine Dioxide
ClO2
Strong oxidant
Generated on-site
  Chlorine gas and sodium chlorite
Algal and phenolic odors
Cost
OH
Phenol
NaClO2

## Slide 82: Benzene ring

## Slide 83: Copper and Copper Sulfate
Copper, Cu, in water supply can cause bluish- green stains
  Maximum Cu level allowed in water supply is 1.3 mg/L
Copper sulfate, CuSO4, might be used to control algae in a reservoir
  Dose is often determined based on alkalinity level
  Recommended maximum dose is 2.5 mg/L as CuSO4
  If adding more than 1.5 mg/L CuSO4, often use chelated Cu (Cu is solubilized).
  At alkalinity less than 50 mg/L, CuSO4 may kill fish.

## Slide 84: Possible Reaction of Cu with Alkalinity
2CuSO4 + 2Na2CO3 + H2O → Cu2(OH)2CO3 +
2Na2SO4 + CO2
Cu2(OH)2CO3 = copper basic carbonate is a precipitate
Where is the alkalinity in reaction?
Might see other Cu complexes form, such as CuCO3, which is soluble, but less toxic than “free Cu.”

## Slide 85: Iron and Manganese
Iron…Fe, 2+ and 3+ forms
  2+ is soluble, ferrous
  3+ is precipitate, ferric
  Yellowish/brownish
Manganese…Mn, 2+ and 4+ common
  2+ is soluble, manganous
  3+ is precipitate, manganic
  Brownish/blackish

## Slide 86: Fe and Mn Control
Oxidize with oxygen, chlorine, chlorine dioxide, potassium permanganate
Oxidizes soluble forms to precipitates; can then sediment or filter out oxidized metal

## Slide 87: Oxidation of Fe
Oxidant | mg Oxidant/mg Fe2+ | mg Alkalinity used/mg Fe2+
Oxygen | 0.14 | 1.8
Chlorine | 0.64 | 2.7
Chlorine dioxide | 1.21 | 2.7
Potassium permanganate | 0.94 | 1.5

## Slide 88: Closer Look at Oxidation of Fe with Oxygen
4Fe(HCO3)2 + O2 + 2H2O → 4 Fe(OH)3 + 8CO2
Identify bicarbonate, oxygen and hydroxide in above equation.
Where is the alkalinity in equation?
What are the charges on iron as a reactant and as a product?
Notes: HCO3 – Bicarbonate
O2 – Oxygen
Hydroxide – OH
HCO3 and OH
Look at Periodic Chart and EW sheet
Reactant – HCO3 is -1 and there are two of them grouped to the Fe, therefore Fe is +2
Product – OH is -1 and there are three of them grouped to the Fe, therefore Fe is +3

## Slide 89: Oxidation of Mn
Oxidant | mg Oxidant/mg Mn2+ | mg Alkalinity used/mg Mn2+
Oxygen | 0.29 | 1.80
Chlorine | 1.29 | 3.64
Chlorine dioxide | 2.46 | 3.60
Potassium permanganate | 1.92 | 1.21

## Slide 90: Closer Look at Oxidation of Mn with Potassium Permanganate
3Mn(HCO3)2 + 2KMnO4 → 5MnO2 + 2KHCO3 + 2H2O + 4CO2
What are the charges on Mn as a reactant and as a product?
Notes: Look at Periodic Chart and EW sheet
Reactant #1 – HCO3 is -1 and there are two of them grouped to the Mn, therefore Mn is +2
Reactant #2 – K is +1 and O is -2, there is one K and four O, therefore Mn is +7
Product – O is -2 and there are two of them grouped to the Mn, therefore Mn is +4

## Slide 92: Road map for this session
General water characteristics
The Periodic Table
Key water parameters
Solutions
Chlorine disinfection
Drinking water applications
Additional exercises & questions

## Slide 93: BUT WAIT, THERE’S MORE! PFAS
Per- and Polyfluorinated Substances (PFAS)
Clothing, adhesives, not-stick cookware, etc.
  Don’t break down in the environment
  Can move through soils, contaminate water
  Bioaccumulate in fish and wildlife
  “Forever chemicals”

## Slide 94: And more and more PFAS!
Per- and Polyfluorinated Substances (PFAS)
  Perfluorooctane sulfonic acid (PFOS)
  Perfluorooctanoic acid (PFOA)

## Slide 95: Practice problems

## Slide 96: Specific gravity
Given that the specific gravity of a solution is 1.76, how much does a gal of the solution weigh? (Assume 4°C)
SG = 1.76 =
X lb/gal = 8.34 lb/gal * 1.76
X = 14.68 lb/gal * 1 gal = 14.68 lb

## Slide 97: 1% Solution
How much KMnO4 (97% pure) should you add to 80 gal of water to make a 1% solution?
% sol’n. = 100[wgt of chem/(wgt of chem + wgt of water)]
  0.01 = wgt of KMnO4/(667.2 lbs + wgt of KMnO4)
(0.01)(667.2) + (0.01)(wgt of KMnO4) = wgt of KMnO4
6.672 lbs + (0.01)(wgt of KMnO4) = wgt of KMnO4
6.672 lbs = wgt of KMnO4 – (0.01)(wgt of KMnO4)
6.672 lbs = (0.99)(wgt of KMnO4)
wgt of KMnO4 = 6.739 lbs
Purity: wgt of KMnO4 = 6.739 lbs / 0.97 = 6.947 lbs

## Slide 98: Dilution problem
If you make a 1:50 dilution of a NaHCO3 solution that has a concentration of 182 mg/L, what is the resulting solution concentration?
182 mg/L *(1/50) = 3.64 mg/L

## Slide 99: Iron problem
How much ClO2 (mg/L) would you suggest be used to treat a water that contains 3 mg/L of Fe2+?
= 3.63

## Slide 100: Objectives for today
Strengthen knowledge/use of water chemistry
Confidence in discussing water chemistry issues
Identify water chemistry’s elements of interest
Practice solving water chemistry problems
Provide a worthwhile use of your time
Prepare you for Short School summary test

## Slide 101: Contact information
David Dawson, PhD, PE
Engineering Field Director
VDH-Office of Drinking Water
407 E. Main Street
Abingdon, VA 24210
Mobile: (276) 739-8587