## Slide 1: Water Fluoridation
Robert D. Edelman, PE
Director, Division of Technical Services
1

## Slide 2: Presentation Outline
What is Fluoride?
Regulations
Fluoride Treatment Chemicals
Fluoride Feed Systems
Monitoring, Record Keeping, and Reporting
Calculations

## Slide 3: What is fluoride?
Fluorine is a chemical element with the symbol F, the lightest halogen, and at standard conditions a pale-yellow gas that is extremely reactive.
Fluoride is an inorganic anion of fluorine, chemical symbol F-
Fluoride and its salts and minerals are important chemical reagents and industrial chemicals.
Fluoride is the simplest fluorine anion.
Fluorine Gas

## Slide 4: Fluorine

## Slide 5: Definition - Fluoridation
Community water fluoridation (herein called simply "fluoridation") is the precise and deliberate upward adjustment in the concentration of the essential trace element fluoride in the public water supply to protect teeth and bones.
The purpose of fluoridation is to reduce the occurrence of tooth decay (cavities).

## Slide 6: Drinking Water Regulations
REGULATIONS
  National Primary Drinking Water Regulations
  National Secondary Drinking Water Regulations
  Virginia Waterworks Regulations

## Slide 7: National Primary Drinking Water Regulations
  MCLG - 4.0 mg/l (40 CFR § 141.51) (Table 546.1)
    Maximum contaminant level goal (MCLG) - maximum level of a contaminant in drinking water at which no known or anticipated adverse effect on the health of persons would occur and that allows for an adequate margin of safety. Maximum contaminant level goals are nonenforceable health goals.
  PMCL - 4.0 mg/l (40 CFR § 141.62) (Table 340.1)
    "Maximum contaminant level" or "MCL" means the highest level of a contaminant that is allowed in drinking water. MCLs are set as close to the MCLGs as feasible using the best available treatment technology.
    PMCL only applies to community waterworks

## Slide 8: National Secondary Drinking Water Regulations
SMCL - 2.0 mg/l (40 CFR § 143.3) (Table 340.1)
  "SMCL" means the secondary maximum contaminant level of a contaminant. SMCLs are based on aesthetic qualities related to the public acceptance of drinking water.
  "Maximum contaminant level" or "MCL" means the maximum permissible level of a contaminant in potable water that is delivered to any consumer of a waterworks. MCLs are set as close to the MCLGs as feasible using the BAT. MCLs may be either "primary" (PMCL), meaning based on health considerations, or "secondary" (SMCL), meaning based on aesthetic considerations.

## Slide 9: Fluoride Compliance Monitoring
Part of Inorganics Panel
Groundwater – one each compliance period (1x/3 years)
  Surface water – annually
Split Sample
  Monthly for comparison to ensure validity of waterworks lab analysis.
  Not a compliance sample.
Notes:   If a single sample exceeds the PMCL:
    Collect confirmation sample and average results together
    If average exceeds the PMCL, begin quarterly monitoring
    Compliance with PMCL is determined on running annual average of 4 quarterly samples
    Continue monitoring until analytical results are reliably and consistently below PMCL.

## Slide 10: MCL EXCEEDANCE
If a single sample exceeds the PMCL:
  Collect confirmation sample and average results together
  If average exceeds the PMCL, begin quarterly monitoring
  Compliance with PMCL is determined on running annual average of 4 quarterly samples
  Provide Public Notice (Tier 2)
  Continue monitoring until analytical results are reliably and consistently below PMCL.
If a single sample exceeds the SMCL:
  Collect confirmation sample
  If avg exceeds SMCL, requires annual public notice.
  Owner shall work with ODW to determine treatment options
Notes:   If a single sample exceeds the PMCL:
    Collect confirmation sample and average results together
    If average exceeds the PMCL, begin quarterly monitoring
    Compliance with PMCL is determined on running annual average of 4 quarterly samples
    Continue monitoring until analytical results are reliably and consistently below PMCL.

## Slide 11: Recent Fluoride Events
EPA’s Fourth Six-Year Review was published on June 23, 2024
  EPA decided not to revise any regulations, including fluoride
  Fluoride was in the category of new information, but no revision recommended due to emerging data
The National Toxicology Program Report - August 2024
  Concluded with “moderate confidence” that fluoride exposure above 1.5 milligrams per liter is associated with lower IQ in children.
  More research is needed to better understand if there are health risks associated with exposure to lower fluoride concentrations.
Federal District Court - Northern District of California – September 2024
  Concluded fluoridated water is an “unreasonable risk”.
  Ignored the NTP report’s conclusions do not apply to lower fluoride levels.
  Instructed EPA to issue a new rule about fluoride in drinking water.

## Slide 12: The new administration
Significant uncertainty with next steps for fluoride with the new Administration
1/29 - EPA Administrator Lee Zeldin approved and sworn in
  Jess Kramer - incoming Assistant Administrator for Water
1/29 – Challenging Senate hearing for Robert F. Kennedy Jr. as nominee for HHS Secretary
  Robert F. Kennedy Jr. said the Trump White House would advise against water fluoridation on January 20
  That action didn’t occur – doesn’t mean it won’t happen later
Multiple potential actions by either EPA, HHS, or CDC (next slides)

## Slide 13: Latest activities
Late March - Utah passed legislation to ban fluoride in drinking water
  Effective May 7, 2025
  Fluoride pump failure in Sandy, Utah in 2019 released excess fluoride
April 7 - EPA announces a review of fluoride health effects
  Timing to complete this review TBD
April 7 - HHS announces plan to stop CDC’s recommendation for community water fluoridation (CWF)
  CWF program at CDC terminated
    CWF website still operational https://www.cdc.gov/fluoridation/index.html

## Slide 14: Latest activities (cont.)
May – Florida legislation signed to ban fluoridation
  Other discussion in other states (LA, TN, ND)
ASDWA developing “What’s Next?”
CDC – no timeline yet for change in CWF fluoridation
EPA – no timeline yet for review of fluoride health effects and both the MCL & SMCL
  Lead and PFAS and other issues are absorbing EPA’s decision-making

## Slide 15: HOW TO FLUORIDATE DRINKING WATER
SINCE FLUORINE DOESN’T EXIST ALONE
MUST FEED A FLUORIDE COMPOUND
TO THE DRINKING WATER SUPPLY
Notes: The cation to which the fluoride is attached should have no undesirable characteristics.
We would not want a compound that had fluoride to give us strong teeth to be connected to a cation that gave us kidney stones – or whatever.
The compound should be relatively inexpensive, so that we can afford to use it, and
It should be readily available.
Lastly, the compound should be safe for water treatment personnel to handle when they follow recommended safety procedures.

## Slide 16: Sodium fluoride – NaF
18
© 2021 Univar Solutions Inc. All rights reserved. Confidential and content subject to change.
Original fluoridation chemical
No current US manufacturing
Label - Toxic (Ingestion, Inhalation)
Absorbed through contact
Requires appropriate PPE for solution make up
Fed using a saturator

## Slide 17: Sodium silicofluoride or sodium fluorosilicate (SSF)
19
© 2021 Univar Solutions Inc. All rights reserved. Confidential and content subject to change.
Very limited US manufacturing
Label - Toxic (Ingestion, Inhalation)
Absorbed through contact
Requires PPE for making up solution
Fed via saturator or dry feeder

## Slide 18: Hydrofluorosilicic acid (HFS)
20
© 2021 Univar Solutions Inc. All rights reserved. Confidential and content subject to change.
23% solution
Made in the USA
Label - Corrosive (contact)
Not an RMP chemical
Fed from bulk storage tank
Minimal handling
Fed using a metering pump
Corrosive fumes (vent outdoors)

## Slide 19: Fluoride Chemical Standards
American Water Works Association
  AWWA B701-24 – Sodium Fluoride
  AWWA B702-24 – Sodium Fluorosilicate
  AWWA B703-24 – Fluorosilicic Acid
NSF International
  NSF/ANSI/CAN Standard 60-2021

## Slide 20: Liquid Chemical Feed – Two Types
    Acid feed systems
      tanks, pumps, auxiliary equipment
    Sodium Fluoride Saturators
      saturator, metering pump, auxiliary equipment

## Slide 21: Liquid Fluoride Feed
26
© 2021 Univar Solutions Inc. All rights reserved. Confidential and content subject to change.
Mechanism
Solution arrives in drums, totes or bulk
Solution fed directly or via day tank
Positive displacement metering pump
Dose level fluoride probe
Advantages
Concentration assay in a lab
Minimal if any daily operator contact
Improved consistency
Reduced waste (especially if bulk or minibulk)

## Slide 22: Liquid fluoride feed
27
© 2021 Univar Solutions Inc. All rights reserved. Confidential and content subject to change.
Indoor or outdoor storage tanks
Day tank- scaled
Minimal operator contact required!
Metering pump

## Slide 23: Acid Feed Systems

## Slide 24: Acid Feed Systems
Notes: Bulk system – same as small only a bulk tank to fill day tank.

## Slide 25: Fluoride Saturators – Sodium Fluoride How do they work?
Operating process
  Chemical bed maintained in tank
  Water flows through chemical bed
  Water becomes saturated
  Saturated solution injected

## Slide 26: Typical Upflow Saturator

## Slide 27: Dry fluoride feed via saturator
25
© 2021 Univar Solutions Inc. All rights reserved. Confidential and content subject to change.
Mechanism
Add dry fluoride and water
Saturated in water to 4%
Saturator and finished tank
Metered in via pump
Dose level fluoride probe
Drawbacks
Routine chemical contact
Saturation accuracy
Shuts down if bed not sufficient
Messy, waste
Cleanout process

## Slide 28: Fluoride Saturators
Process Considerations
  Feed water must be softened if above 50 ppm hardness
  Chemical bed can cake
  Cleaning out impurities

## Slide 29: Fluoride Saturators
Operation
Mark level 100 pounds NaF level on the outside
Add an additional 100 pounds of NaF
Open the water supply valve
Check NaF bed level daily
Add NaF when level drops to 100 pounds
Stir bed occasionally

## Slide 30: Fluoride Saturators
Cleaning
Clean every 12 months or more frequently
Allow NaF level to drop
Disconnect power supply
Disconnect tubing under the cover, remove top
Remove distributor tube (stir if necessary)
Dump bed, flush out tank
Reinstall tube, top, metering pump

## Slide 31: Saturator
A saturator is unique in that the strength of the saturated solution formed is always 18,000 mg/l as F-.
This is due to the fact that sodium fluoride has a solubility that is practically constant (4.0 g/100ml) regardless of the temperature.
This simplifies calculations a great deal
NaF makes 4% wt
Sodium Silcofluoride 0.76% wt

## Slide 32: Dry Chemical Feeders

## Slide 33: Types Dry Feed Equipment
Two types of Dry Feeders
  volumetric
    rotating disk
    oscillating pan
    vibratory pan
    roll
    rotating screw
  gravimetric
    belt type

## Slide 38: Where is Fluoride fed?
Notes: As mentioned earlier today, it is important to remember that we are adding these compounds to the water so that we can adjust the fluoride concentration to the optimal level for the prevention of tooth decay.
The optimal fluoride level for a location is based on the average maximum daily air temperature
And we use the data from a five year period.
This average is for the entire year – we do not recommend changing the optimal level to account for seasonal temperature variations.

## Slide 39: Fluoride solution injection point
All water to be treated must flow past injection point
Place at head of treatment plant?
Keep away from other chemical injection points, especially alum
Need adequate mixing, especially applicable to groundwater systems, may need inline mixer

## Slide 43: Monitoring, Recordkeeping & Reporting

## Slide 44: Monitoring and Recordkeeping
Why You Are Required to Monitor and Keep Records
  To document reliability of fluoridation process
  Crucial for determining dosages of chemicals applied to water

## Slide 45: What Monitoring Is Required?
  Daily fluoride level at entry point
  Water treated by fluoridation process (MGD)
  Monthly Split Fluoride for verification

## Slide 46: Recordkeeping Requirements
Chemical Used (Manufacturer and product name)
Fluoride usage, lb/day
Fluoride dosage, mg/L (daily)
Water Treated, MGD
Finished water (entry point) fluoride concentration, mg/L (maximum, minimum, and average)

## Slide 47: Recordkeeping - Saturators
Date, time and amount of sodium fluoride (NaF) added to saturator
Gallons of make-up water sent to the saturator, recorded daily
Additional records as required for softener if so equipped
Calibration date and calibration curve for metering pump

## Slide 48: Recordkeeping – Dry feeders
Date, time, and amount of sodium fluorosilicate added to hopper of dry feeder
From weight recorder, record weight reading on daily basis. Time of reading must also be recorded. Change recording charts promptly.
Calibration date and calibration curve for volumetric or gravimetric feeder and loss of weight recorder

## Slide 49: Recordkeeping – Acid feed systems
Date, time, and quantity of acid added to day tank if so equipped.
Weight of chemical in day tank or other vessel as indicated by loss of weight recorder. Record on daily basis and note time recorded.
Calibration date and calibration curve solution pump and loss of weight recorder

## Slide 50: Calculations
Notes: As mentioned earlier today, it is important to remember that we are adding these compounds to the water so that we can adjust the fluoride concentration to the optimal level for the prevention of tooth decay.
The optimal fluoride level for a location is based on the average maximum daily air temperature
And we use the data from a five year period.
This average is for the entire year – we do not recommend changing the optimal level to account for seasonal temperature variations.

## Slide 51: Fluoride Dosage Formula
Calculated Dosage:
Fluoride Feed Rate (lb/day) = Dosage (mg/L) x Capacity (MG) X 8.34
AFI X Chemical Purity
REARRANGE TO GET:
Dosage (mg/L) = Fluoride Feed Rate (lb/day) X AFI X Chemical Purity
Capacity (MG) X 8.34
Notes: AFI = Available Fluoride Ion concentration.
In order to find the theoretical concentration of fluoride in the distribution system, the calculated dosage must be determined.
The Fluoride Feed Rate formula can be changed to find the calculated dosage
The Fluoride Feed Rate is changed to Fluoride Fed and the Capacity is changed to Actual Daily Production of water in the water system then the dosage becomes the Calculated Dosage.

## Slide 52: Things you must know…
Desired Dosage: Amount of Fluoride compound needed to obtain desired level
  Desired Dosage = Desired Level – Natural or background Level
Desired Level
  Optimal Level: 0.7 mg/L
Natural Level also known as the background level is the starting level

## Slide 53: Plant Capacity Knows:
Plant Capacity
Maximum capacity
Average capacity
Actual capacity
Minimum capacity
Notes: There are several plant capacity that can be used, and in fact, we will be using more than one in our problems.
The maximum and minimum capacity is obviously the maximum and the minimum amount of water that can be produced each day or year. For example, XX plant has a maximum capacity of 150 MGD.
The average capacity is the amount average amount of water produced on a daily[sometime monthly or yearly] basis. It is used to estimate chemical costs.
The actual daily capacity or production the is the average amount of water produced in a 24 hour period. It is used to determine the calculated dosage

## Slide 54: Fl Compound Specifcs
Chemical Purity & AFI…

## Slide 55: Feed Rate Calculations
After we know our desired dosage, our plant/well capacity and the compound information we can calculate the fluoride feed rate.
Notes: The fluoride feed rate formula is a general equation used to calculate the concentration of a chemical added to water.
The usual units are pounds per day of the fluoride chemical used. Other units can and are used, i.e. lb/hr; kg/ day, etc.

## Slide 56: Dry Feeder Calculations
Dosage (mg/L) = Fluoride Feed Rate (lb/day) X AFI X Chemical Purity
Capacity (MG) X 8.34
From our Fl Specific table, we know for Sodium Fluorosilicate:
AFI = 0.607
Purity = 98.5% (may be different on your product so verify with your vendor)

## Slide 57: Dry Feeder Example
A plant uses 26 lbs. sodium fluorosilicate in treating 1,756,000 gallons of water. What is the calculated dosage?
Dosage (mg/L) = Fluoride Feed Rate (lb/day) X AFI X Chemical Purity
Capacity (MG) X 8.34
AFI = 0.607
Purity = 98.5%
Dosage (mg/L) = 26 X 0.607 X 98.5%
1.756 X 8.34
Dosage (mg/L) = 1.06 mg/L

## Slide 58: Fluorosilicic Acid Calculation
Dosage (mg/L) = Fluoride Feed Rate (lb/day) X AFI X Chemical Purity
Capacity (MG) X 8.34
From our Fl Specific table, we know for Fluorosilicic Acid:
AFI = 0.792
Purity = 23% (may be different on your product so verify with your vendor)

## Slide 59: Acid Calculation
A plant uses 43 lbs. of fluorosilicic acid in treating 1,226,000 gallons of water. Assume the acid is 23 percent purity. What is the calculated dosage?
Dosage (mg/L) = Fluoride Feed Rate (lb/day) X AFI X Chemical Purity
Capacity (MG) X 8.34
AFI = 0.792
Purity = 23%
Dosage (mg/L) = 43 X 0.792 X 23%
1.226 X 8.34
Dosage (mg/L) = 0.77 mg/L

## Slide 60: Saturator Calculations
A saturator is unique in that the strength of the saturated solution formed is always 18,000 mg/l
Sodium fluoride has a solubility that is practically constant (4.0 g/100ml) regardless of the temperature.
This simplifies calculations a great deal
Sodium Silcofluoride 0.76% wt

## Slide 61: Saturator Calculations
Fl feed rate = Capacity X dosage (mg/L)
18,000 mg/L
The calculation here is little different than when using other formula. You will be measuring the fluoride feed typically in gallons. So, you will be entering the gallons of water treated in this formula.

## Slide 62: Saturator Calculations
A plant uses 10 gallons of sodium fluoride solution from its saturation in treating 200,000 gallons of water. What is the calculated dosage?
Dosage (mg/L) = Fl feed rate X 18,000 mg/L
Capacity
Dosage (mg/L) = 10 X 18,000 mg/L
200,000
Dosage (mg/L) = 0.9 mg/L

## Slide 63: QUESTIONS ??
Robert D. Edelman, PE
Director, Division of Technical Services
Robert.Edelman@vdh.virginia.gov (804) 864-7490