## Slide 1: DBP Control - II Theory & Applications
David S. Dawson, PhD, PE
Engineering Field Office Director
VDH-Office of Drinking Water

## Slide 2: Our topics
Disinfection By-Products (DBP) overview
    Drinking water treatment & distribution
DBP Control theory
DBP Control applications
DBP Pilot-scale study (time permitting)

## Slide 3: Our learning objectives
At the conclusion of this presentation:
Describe the two components that react to form DBP
Identify four elements of DBP formation that can be addressed
State two techniques to address DBP formation at the WTP
State two techniques to reduce water age in the distribution system

## Slide 4: Thanks for contributions
Erik Rosenfeldt, Hazen & Sawyer
Jen Miller, CHA
Doug Noffsinger, CH2M-Hill/Jacobs
S.M. Enzler, Lenntech
Lisa Crabtree, VDH-ODW
AWWA & RCAP (EPA-funded project)

## Slide 5: DBP control: theory & Applications

## Slide 6: Our ‘road map’ for today
DBP control theory & background
  Water treatment overview
  What are DBP?
DBP control applications

## Slide 7: Water process diagram

## Slide 8: Overview of water treatment

## Slide 9: History of water treatment - 1
2000 BC – Greek & Sanskrit: boiling and filtration, taste was major focus
1500 BC – Egyptians added alum (coagulation)
800 BC – Elisha pours salt into bad water
500 BC – Hippocrates sieves water to remove sediment (taste issue)
300 BC – Roman aqueducts

## Slide 10: History of water treatment - 2
250 BC – Archimedes invents screw pump
Romans – Build by “rule of thumb”
500-1500 AD – Middle ages (no advancement)
1627 AD – Francis Bacon & filtration
1676 AD – Microscope (van Leeuwenhoek)
1804 AD – 1st WTP (slow sand filtration in Scotland)
1854 AD – London cholera outbreak

## Slide 11: 1854 London cholera epidemic

## Slide 12: London cholera deaths - 1854

## Slide 13: London water pumps - 1854

## Slide 14: History of water treatment - 3
1860+ – Pasteur: germ theory, fermentation, vaccination
1890 – Rapid sand filtration, precede with coagulation and sedimentation
1908 – 1st continuous chlorination in US
20th Century focus – waterborne illness focus, expand to anthropogenic chemicals

## Slide 15: Public Water Supply Disinfection Practices:100 Years and Counting
1902 - first continuous chlorination of municipal drinking water (Belgium)
1908 - first continuous disinfection of municipal drinking water in U.S. NaOCl
1906 WTP use Ozone (Nice, France)
1914 - “It is a matter of common knowledge nowadays that the ultraviolet rays have a strong bactericidal power.”
By 1930s – filtration plus chlorine disinfection virtually eliminates waterborne illnesses in US
Notes: Jersey City NJ
Scientific American Supplement

## Slide 16: Death rate for Typhoid Fever United States, 1900-1960

## Slide 17: US infectious death rate 1900-1996

## Slide 18: Role of disinfection
Primary Disinfection
(at the WTP)
Inactivate microorganisms prior to and through distribution system
Satisfy CT requirements
Typically – free chlorine, ozone, chlorine dioxide

## Slide 19: Role of Disinfection
Primary Disinfection
(at the WTP)
  Inactivate microorganisms prior to and through distribution
  Satisfy CT Requirements
  Typically -- free chlorine, ozone, chlorine dioxide
Notes: CT = chlorine contact time
- pathogens

## Slide 20: Role of Disinfection
Secondary Disinfection
(in distribution system)
  Controls regrowth of microorganisms in system
  Protects against contamination from leaks and corrosion in distribution system
  Indicator of water quality
  Either free chlorine or chloramines
Notes: Personal experience with Chlorine dioxide as secondary disinfection. 10 MGD purchased water from ClO2..

## Slide 21: Role of disinfection
Secondary Disinfection
(in the distribution system)
Controls regrowth of microorganisms in system
Protects against contamination from leaks and corrosion in distribution system
Indicator of water quality
Either free chlorine or chloramines
Notes: Personal experience with Chlorine dioxide as secondary disinfection. 10 MGD purchased water from ClO2..

## Slide 22: Disinfection saves lives!
What could be the downside?
  Acute impact vs chronic impact on public health
“too much of a good thing?”
“everything in moderation?”
Disinfection byproducts …

## Slide 24: What are disinfection byproducts?
Disinfection Byproducts (DBP) are chemicals formed in drinking water by the addition of a disinfectant, such as chlorine, chloramines, chlorine dioxide and ozone, reacting with organic chemicals in the water.

## Slide 25
From IXOM Watercare

## Slide 26: Disinfection byproducts formation
organics + oxidant → DBP

## Slide 27: Our learning objectives
At the conclusion of this presentation:
Describe the two components that react to form DBP
Identify four elements of DBP formation that can be addressed
State two techniques to address DBP formation at the WTP
State two techniques to reduce water age in the distribution system

## Slide 28: What are organics?
Organics are naturally occurring compounds in both groundwater and surface water
Total Organic Carbon (TOC) is a measurement of organics
Typical TOC levels in local groundwater
    0.8 to 5.4 mg/L
Typical TOC levels in surface water
    2.0 to 20.0 mg/L

## Slide 29: Surface water sources of natural organic material (NOM)
Rain events wash organic matter into receiving body.
Flooding reverses flow gradients in upper aquifers
Cavities and fissures in Karst conditions allow surface intrusion
Poor sanitary conditions, i.e., broken seals, abandoned wells, poor locations, result in intrusion
Groundwater with high NOM content indicates the intrusion from Surface Water
Sedimentation, biogrowth, or poor flushing practices
Notes: Natural Organic Matter makes up the humic content in source waters. NOM is either hydrophilic (more soluble in water) or hydrophobic (less soluble and a more aromatic fraction.) Hydrophobic matter is easier to remove in the treatment process.

## Slide 30: Karst conditions
Limestone soluble

## Slide 31: Natural organic material sources

## Slide 32: DBP formation

## Slide 33: Disinfection byproducts formation

## Slide 34: Our learning objectives
At the conclusion of this presentation:
Describe the two components that react to form DBP
Identify four elements of DBP formation that can be addressed
State two techniques to address DBP formation at the WTP
State two techniques to reduce water age in the distribution system

## Slide 35: What affects DBP concentrations?
The concentration of organic chemicals in the source water and treated water
More organics within the WTO and distribution system = increased potential to form DBPs.
Location & amount of disinfectant added to the source water and treated water
Adding chlorine based disinfectants to raw (untreated) source water will immediately begin the reaction to form DBP which normally do not always get removed by the coagulation, flocculation, sedimentation and filtration processes. Furthermore, adding chlorine based disinfectants at higher dosages will increase the reactions for forming DBP.
Treatment process including coagulation, flocculation, sedimentation and filtration
Optimizing the coagulation, flocculation, sedimentation and filtration process to settle or filter out organics should reduce the potential to form DBP.

## Slide 36: What affects DBP concentrations? (continued)
Disinfectant concentration throughout the distribution system
Maintaining a high disinfection residual throughout the distribution system will increase the potential to form DBP.
The water age within a distribution system.
Longer time in contact with disinfectants = higher potential to form DBP.
Biofilms in storage tanks and distribution systems
Biofilms are another source of organics within storage tanks and distribution systems, can react with disinfectants to form DBP
Water temperature
Warmer water has higher potential for forming DBP. (DBP concentrations tend to be higher in the third and fourth quarters of the year)
Notes: Water age in both WTP & distrib system
Good reminder to clean tanks.
Water temperature drives the rate of reaction

## Slide 37: Regulated vs emerging DBP
DBP formation can be controlled by removing precursors before oxidation or using alternate oxidants.
Emerging N-DBPs exhibit orders of magnitude higher cyto- and geno-toxicity than any of the regulated C-DBPs.

## Slide 38: Chlorine chemistry
Cl2 + H2O  HOCl + H+ + Cl-
NaOCl + H2O  Na+ + OCl-
HOCl  H+ + OCl-
Ka = [H+][OCl-]/[HOCl] = 2.611x10-8
pKa = 7.58
the pH of the water affects the relative amounts of HOCl and OCl- present
Notes: HOCl = hypochlorous acid
Hypochlorite ion
HOCl much stronger disinfectant

## Slide 39: Chemistry footnote

## Slide 40: Production of total trihalomethanes (TTHMs)
TTHMs are produced by the reaction of chlorine with organic constituents found in natural waters.
The 4 Trihalomethane compounds of concern are:
  Chloroform (typically >70% inland)
  Bromodichloromethane
  Bromoform (can be >70% coastal)
  Dibromochloromethane
However, Chloroform or Bromoform will always constitute the higher portion of the TTHMs.
Bromoform is produced in coastal areas due to brackish intrusion and varies by well. Bromoform is formed by the reaction of Cl on Bromide.

## Slide 41: DBP formation

## Slide 42: Where TTHMs are formed
High Water Age (MRT)
Storage Tanks with poor water turnover
Low Demand Areas
Stagnant & Slow Moving Water Areas
Dead Ends Pipelines (MRT)
Note: Unlined CI Pipe (systems in existence before 1949) require higher residual chlorine levels
Unlined CI Pipe Tuberculation with Bacterial Growth producing Organic Precursors
Notes: * Side bar on biofilm

## Slide 43: Production of Haloacetic Acids
HAA5s are produced by the reaction of chlorine with organic constituents found in natural waters.
These 5 compounds are regulated as HAA5s.
Monochloroacetic Acid
Monobromoacetic Acid
Dichloroacetic Acid
Dibromoacetic Acid
Trichloroacetic Acid
These compounds begin to degrade a few days after formation.
Notes: Production of haloacetic acids are also formed in a similar fashion as trihalomethanes. When chlorine is added to water containing organic materials both Trihalomethanes and Haloacetic Acids will form. Although there are many haloacetic acids, EPA chose to regulate the 5 compounds that are most commonly formed and pose the biggest health threat.

## Slide 44: Where HAA5 are found
Low demand areas
Toward middle system areas w/ high chlorine concentration and low movement
Near high chlorine dose and/or residual locations
High bacterial growth internal to system
HAA5 will degrade in systems with high water age
Notes: HAA5 degrade over time

## Slide 45: Ratio of TTHM to HAA5
Ratios of TTHM to HAA5 should remain relatively constant
Large variations indicate a change of system conditions
Because HAA5 decay, an increase in HAA5 levels indicates that water age has declined
An increase in both would mean that Cl residuals are too high
Trending of changes can be very valuable for troubleshooting

## Slide 46: Effect of Chlorine dose on DBP production
Typical chlorine doses may range between 2 mg/l to 4 mg/l with chlorine residual leaving the plant at an average near 1.5 mg/l.
Notes: This chart shows the increase in TTHMs and HAA5s associated with increasing the dose of free chlorine. A doubling of the chlorine dose causes a 60% rise in the production of HAA5s and a 23% rise in TTHMs in a short contact period.

## Slide 47: Formation of DBP in a typical water treatment & distribution system
~ 50% Distribution
~ 50% Treatment

## Slide 48: Identifying the point of DBP production in a water system
DBPs are equally produced in the treatment plant and in the WD system.
It is important to note where the DBPs are produced (extra sampling) to identify effective corrective actions.
DBP problems typically occur at MRT Locations.
Proactive DBP Strategies should be targeted.

## Slide 49: Our topics
Disinfection By-Products (DBP) overview
    Drinking water treatment & distribution
DBP Control theory
DBP Control applications
DBP Pilot-scale study (time permitting)

## Slide 50: Development of DBP regulations
Trihalomethane (THM) Rule
Effective in 1979
MCLs: TTHM = 0.100 mg/L (4 THMs)
Quarterly Samples (4 locations – one at max)
Running Annual Averages
Stage 1 D/DBP Rule
Promulgated in 1998; Effective in 2001
MCLs: TTHM = 0.080 mg/L; HAA5 = 0.060 mg/L
Must Demonstrate TOC Removal
Disinfectant Doses Limited
Maintain Specific residuals in Distribution System
Notes: As we know, the Stage 2 D/DBP Rule developed by the USEPA and promulgated on January 4 2006 builds upon regulatory requirements for total trihalomethanes (TTHM) first promulgated in 1979, and more stringent TTHM and haloacetic acid (HAA) limits which became effective in January 2002 under the Stage 1 D/DBP Rule. \

## Slide 51: Development of DBP regulations
Stage 2 D/DBP Rule
Promulgated in 2006; Effective in 2012-13
TTHM & HAA5 same as Stage 1 - 80/60 µg/L
Select IDSE Sites with highest levels
No system wide running annual averages
Use Location running annual average (LRAA)

## Slide 52: Who is required to monitor for DBP & what must be monitored?
Community and Nontransient Noncommunity(NTNC) waterworks that add:
chlorine, chloramines, chlorine dioxide must monitor for TTHM and HAA5.
chlorine dioxide must monitor for chlorite.
ozone must monitor for bromate.
Transient Noncommunity waterworks adding chlorine dioxide to surface water or groundwater under the direct influence of surface must monitor for Chlorite.

## Slide 53: Monitoring requirements for DBP
Waterworks required to monitor for TTHM/HAA5 must collect distribution system samples from approved locations.
Approved monitoring locations selected from sites evaluated in the Initial Distribution System Evaluation (IDSE) or from hydraulic modeling (to determine the average and maximum water age within a distribution system)
Frequency and # of samples to be collected are based on source water type and population served.

## Slide 54: To determine DBP compliance
Calculate the Locational Running Annual Average (LRAA) concentration of TTHM and HAA5 at each sample site. TTHM PMCL is 0.080 mg/L. HAA5 PMCL is 0.060 mg/L. If either TTHM or HAA5 LRAA exceeds the PMCL Levels, the entire waterworks is considered to be in violation.
Compliance for Chlorite is determined by calculating the average of the 3 distribution system samples collected each month. The PMCL for Chlorite is 1.0 mg/L.
Compliance for Bromate is determined by the running annual average, calculated quarterly, of monthly sample results. The PMCL for Bromate is 0.010 mg/L.

## Slide 55: Operational Evaluation Level (OEL)
OEL: a level used to alert a waterworks it may need to act to avoid exceeding the PMCL for TTHM and/or HAA5.
TTHM OEL is calculated by summing the two previous quarters' TTHM results plus twice the current quarter's TTHM result, divided by four. If the calculated OEL > 0.080 mg/L, the waterworks must develop and submit to the ODW an OEL Report within 90 days.
The HAA5 OEL is calculated the same way.
Example Calculation of the OEL:
Q1 TTHM = 0.060 mg/L; Q2 TTHM = 0.070 mg/L; Q3 TTHM = 0.100 mg/L
OEL = [0.060 + 0.070 + (2 x 0.100)] / 4 = 0.0825 mg/L 0.0825 mg/L > 0.080 mg/L mg/L

## Slide 56: TOX and UTOX
Recent attention on total organic halogens (TOX = sum of halogenated DBPs)
EPA and research community concerned about un-identified TOX (UTOX)
Concerns that “emerging” DBPs have greater toxicity
  EPA could consider TOX group approach under new drinking water strategy
How do chlorine and free chlorine match up?

## Slide 58: My perception of how it’s going!
Aberdeen Magazine

## Slide 59: The reality of how it’s going …

## Slide 60: DBP control: theory & Applications

## Slide 61: Our topics
Disinfection By-Products (DBP) overview
    Drinking water treatment & distribution
DBP Control theory
DBP Control applications
DBP Pilot-scale study (time permitting)

## Slide 62: Reducing production of DBP (1 of 2)
Eliminate sources of surface water into production wells
Selecting well blends with lower DBP
Remove precursor material within treatment process
Change the point(s) of chlorine application
Lower the chlorine dose and/or residual
Use alternate disinfection strategies

## Slide 63: Reducing production of DBP (2 of 2)
WTP processes are absent of organic growth (i.e., ion exchange and activated carbon systems)
Water Tank Turnover
Reduce Distribution System Water Age
Flush water in slow moving areas and at dead-ends
Remove sediment that creates chlorine demand
Remove biofilm that converts inorganic to organic materials

## Slide 64: Where address DBP?

## Slide 65: DBP control applications
At the water treatment plant
In the distribution system

## Slide 66: WTP applications
Disinfection strategies
Optimize WTP processes (coagulation)
Powered Activated Carbon (PAC)
UV
Ozone/Biofilters
Chloramines
Granular Activated Carbon (GAC)

## Slide 67: Disinfectant Strategies
Reduce Dosing Concentration of Disinfectant
Change Points of Application
Change forms of Disinfectant
Use of Multiple Disinfectants
Change Disinfectant
Use of Orthophosphate in WD systems that use unlined CI Pipe
Notes: Excess free chlorine in the presence of organic materials in the water will result in higher levels of DBP. For this reason use of chlorine prior to removal of TOC should be minimized. Fortunately chlorine is more effective in warmer weather and smaller doses may still be effective.
Another method found to be successful is to change the points of application to minimize the contact with untreated surface water. DBP formation has found to be reduced as much as 50% when disinfection follows the coagulation process.
Some water systems have elected to use chloramines instead of chlorine. Chloramines are significantly less reactive but still provide for the inactivation of pathogens. Chloramines are produced by the addition of ammonia.
Some systems have elected to use multiple disinfectants. For example, free chlorine may be used as the primary disinfectant and chloramines are used to provide disinfectant residual. Injection of ammonia with chlorine forms chloramines and has a much lower potential of forming Disinfection By-Products, like Trihalomethanes.
Because of the inability to control the production of DBP, alternatives disinfectants such as Ozone; Chlorine Dioxide; Potassium Permanganate; Ultraviolet Light; and Advanced Oxidation Processes.

## Slide 68: Chlorination Strategies
Primary Chlorination
rapid mix
flocculation
sedimentation
filtration
disinfection& storage
distribution
Prechlorination
Raw water intake
Booster Chlorination
Chloramine Conversion
Prechlorination |  | 
Oxidation of Fe & Mn Biogrowth control Long CT |  | 
Prechlorination | Primary Chlorination | 
Oxidation of Fe & Mn Biogrowth control Long CT | After TOC removal Pre-filter: longer filter runs Post-filter: bioremoval of TOC | 
Prechlorination | Primary Chlorination | Booster Chlorination
Oxidation of Fe & Mn Biogrowth control Long CT | After TOC removal Pre-filter: longer filter runs Post-filter: bioremoval of TOC | Keeps driving force low
Notes: *ANIMATION
Different points of chlorination discussed earlier in module 3
Different chlorination strategies are used for achieving different treatment objectives as shown in the Table above

## Slide 69: Effects of Moving the Point of Disinfection
Moving the Point of Disinfection acts in three ways:
Decreases significantly the time that the highest free chlorine concentration is in contact with organic material.
Treatment, especially coagulation, sed. and filtration removes a portion of the TOC.
In combining 1 & 2 above, the dose requirement for chlorine is lower and easier to predict
Surface Water Process Treatment provides significant TOC reduction. However, any treatment process used provides some level of TOC reduction.
Notes: Moving the point of disinfection is effective because TOC is being removed at each step in the treatment process. By moving the application point from a pre-chlorination point to a post sedimentation point in this example both THM and HAA5s have been reduced by over 50%!

## Slide 70: Permanganate to Remove TOC
Long Used for Taste and Odor
Removes color forming substances - the same constituents that cause DBP formation
Dosage varies from 0.25 mg/l to 20 mg/l with water quality
Average dosage is 2 to 4 mg/l - 30% TOC removal efficiencies reported
Limitation - can not be used in systems with high Sulfide levels or with changing conditions

## Slide 71: Effective Chlorination System Modification Strategies
Disinfection
Location
Action
Benefit
Chlorine Feed
Reduce chlorine feed rates while maintaining proper chlorine residuals
Fewer DBPs formed in the water system. No / little cost for this option.
Chlorine Injection Point
Change point of chlorine injection to reduce the age of chlorinated water
Fewer DBPs formed in the water system. Small cost for this option.
Chlorine Injection Boosters
Add chlorine injection point(s) to boost Chlorine residuals in the distribution system instead of at the plant
Lower total chlorine added at the plant site. DBPs formed in the distribution system.
Alternate Disinfection / Application
Use of chloramines in distribution systems with long detention times or selective use of preoxidation or oxidant such as NaMnO4
Fewer DBPs formed in the water system. Costs for this option could be significant.
Notes: Because in excess of 90% of the water treatment plants use chlorine as the primary disinfectant, adopting modifications to disinfection strategies can be very effective in reducing the production of DBP. These modifications are generally much more cost effective than changing treatment processes or using alternative disinfectants.

## Slide 72: WTP applications
Disinfection strategies
Optimize WTP processes (coagulation)
Powered Activated Carbon (PAC)
UV
Ozone/Biofilters
Chloramines
Granular Activated Carbon (GAC)

## Slide 73: Coagulation to Remove TOC
TOC Alkalinity (CaCO3)
(Mg C/L) 0-60 60-120 >120
2.0 to 4.0 35% 25% 15%
4.0 to 8.0 45% 35% 25%
>8.0 50% 40% 30%
TOC Removal using Enhanced Coagulation for Surface Water Plants (Treatment Technique)
Typically Alum is used and requires sedimentation/filtration Lime can also be used but has less ability due to high pH
Notes: This slide shows the amount of TOC that can be removed for different TOC and alkalinity concentrations in a raw water using enhanced coagulation. While conventional coagulation jar testing is concerned with removal of colloidal materials. enhanced coagulation is used to determine the amount of coagulant that is most effective for TOC removal.

## Slide 74: WTP applications
Disinfection strategies
Optimize WTP processes (coagulation)
Powered Activated Carbon (PAC)
UV
Ozone/Biofilters
Chloramines
Granular Activated Carbon (GAC)

## Slide 75
Powdered Activated Carbon (PAC)
dist.
PAC
PAC
PAC
PAC
Intake
PAC
B/W
Application Point | Intake | PAC Contactor | Rapid Mix | Flocculation | Sedimentation
Contact Time (min) | varies | 15 – 90 | < 5 | 30 - 60 | 120 - 240
Mixing | poor | excellent | very good | moderate | none
PAC removal
PAC removal
Notes: *ANIMATION
PAC is most frequently used for the control of taste and odor, even though it can be used for the removal of DBP precursors.
The effectiveness of PAC in adsorbing tastes and odors depends on adequate mixing, contact time, dosage, and on the cause and concentration of the taste/odor problem.
Mixing and contact time are determined by the location at which the PAC is added in the treatment process, so adjustments made by the operator will usually involve only dosage adjustments.
The dosage usually ranges from 1 to 15 mg/L for taste and odor removal, but dosage must be much higher, in the range of 100 mg/L or more, when the PAC is being used to remove trihalomethanes or trihalomethane precursors. An appropriate dosage should be selected using jar tests.

## Slide 76: WTP applications
Disinfection strategies
Optimize WTP processes (coagulation)
Powered Activated Carbon (PAC)
UV
Ozone/Biofilters
Chloramines
Granular Activated Carbon (GAC)

## Slide 77: Evolution of UV disinfection for drinking water
Several large utilities installing UV disinfection (Albany, Pittsburgh, Seattle …)
2001
Over 1000 small installations in Europe
1996
Germicidal Impact of Sunlight Observed
1887
UV disinfection found to inactivate Crypto
1998
First drinking water facility in Marseilles
1910
Reliable UV facilities demonstrated in Austria and Switzerland
1955
UV lamp invented
1901

## Slide 78: Kristen M. Lentz WTP - 2010
Treatment Process:
Ammonia
Rapid Mix
Floc/
Sed
Filters
Disinfection
In Clearwells
Pump/
Storage
Storage
FW
Pumps
Chlorine
Enhanced Coagulation with Ferric Sulfate at Depressed pH
Chlorinate Upstream of Filters for Mn Control
Add ammonia to form chloramines in finished water
DBP Control Strategy:
  Enhanced Coagulation
  Chloramines in Distribution System
Notes: Norfolk Virginia

## Slide 79: Kristen M. Lentz WTP - 2010
4.0 MG
FW Storage Tank
Floc/Sed
(above)
Clearwells
(below)
Filter Bldg
Residuals PS
High Pressure PS
Backwash Equalization Basin
Intermediate Pump Station
Chemical/Operations Bldg

## Slide 80: Multiple barrier disinfection approach to meet DBP and disinfection goals
Rapid Mix
Floc/
Sed
New Filters
Clearwell
SW
Storage
Storage
FW
Pumps
New SW Pumps
Low Lift Pumps
Ammonia
Chlorine
UV
Chlorine Fed Upstream of Filters to Maintain Mn Control
Free Chlorine Contact Time can be Limited to 10-12 minutes at Design Flows (0.5-log Giardia Inactivation)
  Achievable in Deep Bed Filters and Downstream PS Wet Well
UV Sized to Provide a Minimum 1-log Giardia Inactivation with One Reactor Out of Service
  Conservative Design Dose = 40 mJ/cm2
Ammonia is Added Immediately Downstream of UV

## Slide 81: Multiple barrier disinfection approach to meet DBP and disinfection goals
Disinfection Process Enhanced by Adding a Second Disinfection Barrier
Design Free Chlorine Contact Time Achieves 0.5-log Giardia Inactivation
City’s 60/40 DBP Goals Achieved
Change Allowed VDH to Modify Disinfection Backstop Requirement to 4-log Giardia
Overall Settled/Finished Water Storage Volumes Maintained

## Slide 82: Multiple barrier disinfection approach meets DBP and disinfection goals
Safeguards drinking water against most microorganisms treated by chlorine
Inactivation of chlorine-resistant protozoa, including Cryptosporidium and Giardia
TrojanUV

## Slide 83: K.M. Lentz WTP Phase III flow diagram

## Slide 84: Kristen M. Lentz WTP site layout

## Slide 85: WTP applications
Disinfection strategies
Optimize WTP processes (coagulation)
Powered Activated Carbon (PAC)
UV
Ozone/Biofilters
Chloramines
Granular Activated Carbon (GAC)

## Slide 86: Monitored Parameters
 | Carbonaceous DBPs | Nitrogenous DBPs
 | Trihalomethanes | Halonitromethanes
 |  | Haloacetonitriles
 | Haloacetic Acids | 
 |  | Nitrosamines
 | Water Quality Parameters
 | DOC (mg-C/L)
 | DN (mg-N/L)
 | UV254 (Abs./cm)
 | Br- (µg/L)
 | NO3- (µg/L)
 | NO2- (µg/L)
 | SO4-2 (µg/L)
 | O3 (mg/L)
 | NH3 (mg/L)
 | pH
 | Free/Combined Chlorine Residual (mg/L)
Notes: *ANIMATION

## Slide 87: Biofiltration Basics
Conventional Treatment Process
Cl2
Cl2
Aerobic Biological Treatment
Notes: *ANIMATION
Employ biodegradation, adsorption, and filtration of solids

## Slide 88: Holistic Biofiltration Example: Stability
Stability in Distribution can be a function of Biodegradable Carbon (BDOC/AOC)
r
Rapid Mix
UV
Raw
Water
Coagulant, PAC, KMnO4, Cl2?
Floc / Sedimentation
Ozone
Filtration / Biofiltration
Cl2
Distribution
Chlorine Contact
NH3?
Chart: 
| AOC | NBDOC
AOC NBDOC | 0.1 | 0.9
Raw TOC
= 6.67 mg/L
NBDOC = 90%
AOC = 10%
AOC = 10%
NBDOC = 90%
Settled TOC = 2 mg/L
Chart: 
| AOC | NBDOC
AOC NBDOC | 0.1 | 0.9
Chart: 
| AOC | NBDOC
AOC NBDOC | 0.2 | 0.8
AOC = 20%
NBDOC = 80%
Post-Ozone TOC = 2 mg/L
Chart: 
| AOC | NBDOC
AOC NBDOC | 0.2 | 0.8
Conventional Filter
TOC = 2 mg/L
AOC = 400 ug/L
Biofiltration
(75% AOC Removal)
TOC = 1.7 mg/L
AOC = 100 ug/L
Notes: *ANNIMATION
AOC = assumable organic carbon

## Slide 89: Holistic Biofiltration Example: T&O
Algae Derived Taste and Odor (MIB and geosmin)
r
Rapid Mix
UV
Raw
Water
Coagulant, PAC, KMnO4, Cl2?
Floc / Sedimentation
Ozone
Filtration / Biofiltration
Cl2
Distribution
Chlorine Contact
NH3?
Raw Water MIB/geosmin
Notes: *ANNIMATION

## Slide 90: Balancing components of biofilters
Turbidity Removal
Contaminant Removal
Hydraulic Performance
Biology
Physics
Chemistry
Collector Efficiency
Backwash, Pretreatment?
Biological Growth
Nutrients Ratios, AOC, EPS, ATP
Role of Pretreatment
Coagulation, Oxidation
Design
and
Operations

## Slide 91: Time for a short break?

## Slide 92: WTP applications
Disinfection strategies
Optimize WTP processes (coagulation)
Powered Activated Carbon (PAC)
UV
Ozone/Biofilters
Chloramines
Granular Activated Carbon (GAC)

## Slide 93: History of chloramines

## Slide 94: Utilities with long experience
St. Louis 1934
Boston 1944
Indianapolis 1954
Minneapolis 1959
Dallas 1969
Philadelphia 1982
Miami 1982

## Slide 95: Chloramine benefits
Good TTHM/HAA5 control
Longer lasting secondary disinfectant residual than free chlorine
Biofilm control
Minimize Cl2 Taste & Odor
Widely practiced
Relatively inexpensive
Short Implementation time

## Slide 96: DBP Formation with Chlorine and Chloramines
primary disinfection
with free chlorine
Chloramines
(ammonia added)
Secondary disinfection with chloramines
Free Chlorine
Time
DBP Concentration
WTP
Distribution System

## Slide 97: Chloramine drawbacks
Less effective than Cl2 as disinfectant
Other potential by-products (e.g., NDMA)
Nitrification
Potentially harmful to some plumbing materials
3rd party impacts (e.g. kidney dialysis, fish)

## Slide 98: Chloramine Chemistry
HOCl
+
(Dichloramine)
H2O
+
NHCl2
NH2Cl
HOCl
+
NHCl2
H2O
+
NCl3
(Trichloramine)
HOCl
H2O
+
+
NH2Cl
NH3
(Monochloramine)
(Hypochlorous acid)
(Ammonia)
Chloramines are formed when Cl2 reacts with ammonia (NH3)
  Cl2:NH3-N < 5:1
  Cl2:NH3-N > 5:1

## Slide 99: Disinfection with Clint Eastwood

## Slide 100: The Good, the Bad, and the Ugly
Monochloramine (the good)
  Effective disinfectant
  Preferred form
Dichloramine (the bad)
  Taste and odor problems
  Decreased residual stability
  Poor disinfectant
Trichloramine (the ugly)
  Ineffective disinfectant
  Taste and odor problems
NH Cl
2
NHCl
2
NCl3
Notes: *ANIMATION

## Slide 101: Chloramine speciation
The species formed depends on:
ratio of chlorine to ammonia (very high ratio can form N2)
temperature
pH high pH (>7.5) favors monochloramine
Cl2:NH3-N Ratio | Dominant Species
< 5:1 | Monochloramine
5:1 to 7.6:1 | Dichloramines
> 7.6:1 | Free Chlorine
Source: Palin, 1950

## Slide 102: pH
pH > 7.5 is desirable for:
Stability of monochloramine residual
Avoiding taste & odor associated with dichloramines and trichloramines

## Slide 103: Nitrification in the distribution system
Factors affecting the potential for nitrification include:
  Temperature
  Chlorine-to-ammonia ratio
  Free ammonia concentration
  Chloramine dose
  Water age
  Reservoir mixing and turnover

## Slide 104: Future chloramine byproducts regulation?
Nitrosodimethylamine (NDMA) may be regulated in the future
Other oxidants currently have DBPs: Ozone, Chlorine, etc.

## Slide 105: Advantages with chloramines
Not as reactive with organic compounds -- significantly less DBPs will form
Residual is more stable & longer lasting
Provide better protection against bacterial regrowth in systems with large storage tanks & dead-end water mains (when residuals are maintained)
Fewer taste & odor complaints because chloramines do not react with organic compounds.
Inexpensive
Easy to make

## Slide 106: Chloramine disadvantages
Not as strong as other disinfectants
  (e.g., Chlorine, Ozone, & Chlorine dioxide)
Cannot oxidize Iron, Manganese, & Sulfides
Sometimes necessary to periodically convert to free chlorine for biofilm control in the water distribution system (burn lasting 2 to 3 weeks)
Less effective at high pH
Forms like dichloramine cause treatment & operating problems
Excess ammonia leads to nitrification
Problem maintaining residual in dead-ends & other locations

## Slide 107: WTP applications
Disinfection strategies
Optimize WTP processes (coagulation)
Powered Activated Carbon (PAC)
UV
Ozone/Biofilters
Chloramines
Granular Activated Carbon (GAC)

## Slide 108: Activated carbon filter
For Source Water TOC from 2 to 4 mg C/L, activated carbon systems typically remove >50%
Activated carbon comes in two forms:
- Powdered Activated Carbon (PAC)
- Granular Activated Carbon (GAC)
Removal mechanisms are the same

## Slide 109
Conventional treatment with filter media replaced with GAC
disinfectant
rapid mix
flocculation
settling
disinfection& storage
distribution
coagulant
GAC filter-adsorber
Granular Activated Carbon (GAC): Filter Adsorber (FA)
Notes: GAC has an extremely large amount of adsorption surface area, generally around 73 acre/lb (650 m2/gram) to 112 acre/lb (1000 m2/gram).
GAC is made of tiny clusters of carbon atoms stacked upon one another, and is produced by heating the carbon source (coal, lignite, wood, nutshells or peat) in the absence of air which produces a high carbon content material.
As listed by USEPA, GAC is Best Available Technology for the following contaminants:
• Disinfection Byproducts (DBPs) • Mercury and Cadmium • Natural Organic Matter
• Synthetic Organic Chemicals (specifically: benzo(a)pyrene, di(2-ethylhexyl)adipate, di(2- ethylhexyl)phthalate, hexachlorobenzene, dioxin)
• Radionuclides

## Slide 110
Conventional treatment with additional GAC filter
disinfectant
rapid mix
flocculation
settling
rapid media filtration
disinfection& storage
Dist.
coagulant
GAC filtration
Granular Activated Carbon (GAC): Post Filter Adsorber (PFA)
Application | EBCT (min) | TOC Removal (%) | Media Life | Media size | Limitations
Post-Filter Adsorber | 5 - 30 | 10 - 70 | 2 - 24 months | 12x40 ES= 0.65 mm | Cost/space/hydraulic head Oxidant compatibility
Notes: *ANNIMATION
Advantages of GAC Post-filter Contactors over GAC/sand and dual-media filters are the following:
Longer empty-bed contact time (EBCT) in post filter contactors – i.e., larger media depth resulting in higher organics removal
Post filter GAC contactors do not have to be used year round since it is not part of the filters.
Less frequent regeneration/replacement of the GAC compared to GAC filter adsorbers
Post filter contactors also allow separation of two processes for turbidity and DOC removal. Filters can then be optimized for turbidity removal, while post-filter contactors used for TOC removal

## Slide 111: Our learning objectives
At the conclusion of this presentation:
Describe the two components that react to form DBP
Identify four elements of DBP formation that can be addressed
State two techniques to address DBP formation at the WTP
State two techniques to reduce water age in the distribution system

## Slide 112: DBP control applications
At the water treatment plant
In the distribution system

## Slide 113: Distribution system applications
Reduce water age
Storage tank mixing & aeration
Introduce chlorine throughout system

## Slide 114: Typical distribution system water age (days)
Population | Miles of main | Min RT | MRT
> 750,000 | >1,000 | 1 day | ~ 1 wk
< 100,000 | < 400 | 1 day | ~ 2 wks
< 25,000 | < 100 | 1 day | ~ 1 mo.
AWWA: Water Age for average and dead-end conditions
Notes: Many water distribution systems have extremely high water ages. Water with high water age will frequently not have enough chlorine residual leading to growth of bacteria in dead end distribution lines and in storage tanks. The sediment that has been deposited in the dead end lines and in the water tanks will contain concentrations of compounds that will support biological growth.

## Slide 115: Water age & DBP production
Franchi and Hill, 2002
Two slopes are present in TTHM development.
-The first is most significant and is related to Cl dose.
-The second is slower and related to Cl residual
Cl dose
Cl Residual
Notes: This plot shows the relationship to TTHM formation and residence time. Note that the chloramine shows little change in TTHM formation until after a period of a couple of days. In this case the chloramine has been biodegraded to free chlorine and is now producing TTHMs at the same rate as the free chlorine.

## Slide 116: Reduce Water Age
Flush at optimal locations and flows
Bleed water at zone boundaries
Increase tank turnover
Control VFDs advantageously
Use ground storage and control valves to circulate water
Close valves to change flow patterns
Change operating methods with low flows
Reduce storage volume in low demand zones
Eliminate dead-ends
Notes: Every distribution system is unique and some things can work better than others

## Slide 117: Flushing Objectives Used in Water Distribution Systems
Unidirectional Flushing
> 2.5 fps velocity that removes solid deposits and biofilm from pipelines
Conventional Flushing
< 2.5 fps velocity that reduces water age, raises disinfectant residual removes coloration
&

## Slide 118: Effects of pH on the Production of DBPs in Distribution System
pH
Note:
HAA5
Amy et al. 1987
Franchi et al. 2002
TTHM and HAA% Formation Potential
Notes: The graph on the left shows the effects of pH in the production of THMs over a 150 hour period. It can be seen that as the pH rises more TTHMS are produced.
The plot on the right shows the same situation compared to HAA5 production. It can be observed that HAA5s are less susceptible to pH increases and actually have decreased. This is due to the biodegradation of the HAA5 over a long period of time.

## Slide 119: Distribution System applications
Reduce water age
Storage tank mixing & aeration
Introduce chlorine throughout system

## Slide 120: Water Turnover in Tanks
Storage tank water movement
Daily goal of 50% storage volume removed
Minimum of 20% - 30%
Target of every 3 days
Increasing bacterial growth:
protection from UV
moderate high temperature
mildly alkaline pH (7.4 – 8.4)
O2 present
substrate for growth
Notes: Sediments are the ideal place for development of biofilm since all conditions needed for bacterial growth are provided. Bacteria that are slow growing can colonize in these biofilms and produce compounds that exert high chlorine demands. Since the bacteria are protected from chlorine by the biofilm typical chlorination practices will not be effective.
These biofilms can cause other problems too such as turbidity, taste and odor problems that may be pronounced in certain areas of the distribution system.
Removal of the sediments that support these conditions is the most effective way of addressing the problem.

## Slide 121: Problems with Sediments in Tanks
Sediments contain significant concentrations of organic nutrients and exert a disinfectant demand (leads to higher Cl doses)
Sediments provide protective layers for biofilms (allows pathogens to repair)
Sediments encourage the growth of slow growing nitrifying bacteria (lowers Cl residual)
Bacteria contribute organics (leads to formation of DBP)
Bacterial growth (leads to turbidity, taste and odor problems that require higher Cl dosages)
Notes: Sediments are the ideal place for development of biofilm since all conditions needed for bacterial growth are provided. Bacteria that are slow growing can colonize in these biofilms and produce compounds that exert high chlorine demands. Since the bacteria are protected from chlorine by the biofilm typical chlorination practices will not be effective.
These biofilms can cause other problems too such as turbidity, taste and odor problems that may be pronounced in certain areas of the distribution system.
Removal of the sediments that support these conditions is the most effective way of addressing the problem.

## Slide 122: Wythe County Tank Aeration System

## Slide 126: Full-Scale Installation 7.5-hp aerator installed in 2 MG reservoir
Notes: Instructors please describe the photos as that of an actual surface aerator in the Phoenix, AZ area.
Top left hand photo is that of the distribution system reservoir site
Bottom left hand photo is the surface aerator in operation.
Middle photo is the inside of the reservoir that shows the mooring posts of the surface aerator.
Top right hand photo is that of the ventilation fan. It is always recommended to keep reservoir headspace under positive pressure. That is why ventilation fan is used.
Bottom right hand photo is that of the access hatch at the top of the reservoir through which the surface aerator is installed in the reservoir.

## Slide 127: TideFlex Tank Mixing Assembly

## Slide 128: Distribution System applications
Reduce water age
Storage tank mixing & aeration
Introduce chlorine throughout system

## Slide 129: Introduce chlorine throughout the distribution system
Reduce dosage at WTP
Tailor rechlorination to distribution system needs

## Slide 130: Distribution System applications
Reduce water age
Storage tank mixing & aeration
Introduce chlorine throughout system

## Slide 131: Our learning objectives
At the conclusion of this presentation:
Describe the two components that react to form DBP
Identify four elements of DBP formation that can be addressed
State two techniques to address DBP formation at the WTP
State two techniques to reduce water age in the distribution system

## Slide 132: Our topics
Disinfection By-Products (DBP) overview
    Drinking water treatment & distribution
DBP Control theory
DBP Control applications
DBP Pilot-scale study (time permitting)

## Slide 133: How are we doing for time?

## Slide 134: A pilot study

## Slide 135: No Silver Bullet: a lesson on synergy of small operational changes in a study of DBP reduction in low TOC source water
Jennifer Miller, PhD, PE, Lisa Crabtree (VDH), Bill Pedigo, DJ Farmer, & David Peyton (Town of Pulaski)
Presented at WaterJAM 2022

## Slide 136: Project Goals
Meet TTHM and HAA5 MCLs in the distribution system.
Implement “low hanging fruit” improvements at the WTP for process optimization to reduce precursors and oxidant demand, and strategically apply chlorination.
Use hydraulic modeling to identify options to reduce high water age, including reductions in water storage capacity, and combining pressure zones.
Plan for additional capital improvements if further DBP reductions are shown to be necessary.

## Slide 137: Full-Scale Pilot Test questions
Can UV254 serve as an indicator for DBPs?
Does PAC help with precursor removal?
What impact do clarifier operations have on precursor removal and DBP formation?
Would a different coagulant improve clarifier operations?
Does permanganate, as a pre-oxidant, reduce chlorine demand (and by extension, DBP formation)?
What impact do chlorination practices have on DBP formation?

## Slide 138: Distribution System –water age

## Slide 139: Our learning objectives
At the conclusion of this presentation:
Describe the two components that react to form DBP
Identify four elements of DBP formation that can be addressed
State two techniques to address DBP formation at the WTP
State two techniques to reduce water age in the distribution system

## Slide 140: Marion, Virginia water tanks

## Slide 141: The Peachoid

## Slide 142: For follow up
Please contact:
David Dawson, PhD, PE
Engineering Field Director - Abingdon
VDH Office of Drinking Water
(276) 698-4906
david.dawson@vdh.virginia.gov