## Slide 1: Water Treatment Plant Operators Short Course
Filtration

## Slide 2: Goals for Today
Filtration Objectives and Mechanisms
  Turbidity
  Water chemistry
  Adsorption vs. Absorption
  Filter design
Gravity Filtration
  Slow, High, and Rapid Rate Filtration
Filter Operations
  Flow Control
  Underdrains
  Backwashing

## Slide 3: FILTRATION OBJECTIVES

## Slide 4: Why Filter?
1989 – EPA SWTA (Surface Water Treatment Rule) regulations:
  Required filtration
  Set limits on turbidity
  Regulated recycling of residual flows
Applies to all surface water and groundwater under influence of surface water

## Slide 5: Filtration Objectives - Turbidity
Remove suspended and colloidal matter (turbidity)
Debatably most important role of filtration – removal of microbes
  Algae, bacteria, and viruses
  Esp. those with high resistance to disinfectants
Low NTUs associated with low microbe count

## Slide 6: Log Removal = Log10 (Influent Counts/Effluent Counts)
Percent Removal | Log Removal (LRV) | Example
90 | 1 | Log10(10/1)
99 | 2 | Log10(100/1)
99.9 | 3 | Log10(1,000/1)
99.99 | 4 | Log10(10,000/1)
99.999 | 5 | Log10(100,000/1)

## Slide 7: Turbidity
Measure of suspended solids in water
Measured as NTU – nephelometric turbidity units
VOP Goal: Filtered water turbidity of less than or equal to 0.1 NTU in at least 95% of monthly samples
Notes: ODW Virginia’s Optimization Program Manual

## Slide 8: Filtration Objectives - Chemistry
Change the chemical characteristics of the water
  Naturally Occurring Organic Matter (NOM)
  Total Organic Carbon (TOC) – humic and fulvic acids
  Color

## Slide 9: Natural Organic Matter (NOM)
Broad term - complex mix of thousands of organic compounds in water
Formed from decaying plant and animal matter
Coagulation - dissolved NOM coverts to a solid so able to be removed during filtration
Why measure?
  High NOM indicates high potential for disinfection byproducts (DBPs)
Notes: high SUVA indicates a large portion of humic matter present in the water,
Since aromatic organics have a greater tendency to react with disinfectants to create DBPs, a high SUVA indicates there is a greater potential for the formation of DBP’s.
SUVA values less that 2 - low chlorine demand and low THM formation potential.
SUVA values between 2 and 4 -medium UV absorbance a higher chlorine demand and higher THM formation potential.
SUVA values in excess of 4 -associated with high UV absorbance, high chlorine demand and a high THM formation potential.

## Slide 10: NOM Removal
Will revisit this with Zeta Potential
Notes: high SUVA indicates a large portion of humic matter present in the water,
Since aromatic organics have a greater tendency to react with disinfectants to create DBPs, a high SUVA indicates there is a greater potential for the formation of DBP’s.
SUVA values less that 2 - low chlorine demand and low THM formation potential.
SUVA values between 2 and 4 -medium UV absorbance a higher chlorine demand and higher THM formation potential.
SUVA values in excess of 4 -associated with high UV absorbance, high chlorine demand and a high THM formation potential.

## Slide 11: Measurement of NOM
Specific ultraviolet absorbance (SUVA)
  DOC measured by filtering sample (0.45 micron) and analyzing for TOC
SUVA values
  < 2 = low chlorine demand and low THM formation potential
  2 - 4 = medium UV absorbance a higher chlorine demand and higher THM formation potential
  > 4 = high UV absorbance, high chlorine demand and a high THM formation potential
Notes: high SUVA indicates a large portion of humic matter present in the water,
Since aromatic organics have a greater tendency to react with disinfectants to create DBPs, a high SUVA indicates there is a greater potential for the formation of DBP’s.
SUVA values less that 2 - low chlorine demand and low THM formation potential.
SUVA values between 2 and 4 -medium UV absorbance a higher chlorine demand and higher THM formation potential.
SUVA values in excess of 4 -associated with high UV absorbance, high chlorine demand and a high THM formation potential.

## Slide 12: FILTRATION MECHANISMS

## Slide 13: Filtration Categories
Driving Force
  Gravity
  Pressure (sand, membrane and ion exchange)
Hydraulic loading rate
  Slow Sand (0.05 – 0.13 gpm/ft2)
  Rapid Sand (1 – 2 gpm/ft2)
  High Rate (3 – 15 gpm/ft2)
Media configuration
  Slow Sand
  Rapid Sand
  Mono Media
  Mixed Media (dual and tri-media)

## Slide 14: Filtration Mechanisms
Depth filtration – retains large mass of particles before backwash (particle transport)
Straining - Removes particles of suspended matter that are too large to pass through the openings between media
Biological mat - Facilitates removal of colloidal matter and bacteria that are too small to be removed by mechanical straining
Removal Mechanism
Depth Filtration
Straining or Sieving
Cake/Biological Filtration

## Slide 15: Gravity Filtration
Slow sand (0.05 – 0.13 gpm/ft2)
Dual media
  Rapid rate (1 – 2 gpm/ft2)
  High rate (3 – 15 gpm/ft2)
Tri or Multimedia
Each has its own
  Advantages and disadvantages
  Purposes
  Capabilities and Limitations

## Slide 16: Filter Loading Rate (or HLR)
Measurement of the volume of water applied to each filter unit of filter surface area
Flow rate into the filter divided by the total filter area

## Slide 17: Filter Loading Rate (or HLR)
A slow sand filter is 15 FT wide and 25 FT long. If the filter receives a flow of 35,600 GPD, what is the loading rate in GPM per FT2 ?

## Slide 18: Filter Loading Rate (or HLR)
A slow sand filter is 15 FT wide and 25 FT long. If the filter receives a flow of 35,600 GPD, what is the loading rate in GPM per FT2 ?
GPM =
Filter area =
Filter Loading Rate (HLR) =

## Slide 19: Filter Capacity
A filter has an average flow rate of 2,250 GPM. How long, in hours, will the filter need to run to produce 730,000 gallons of filtered water?

## Slide 20: Filter Capacity
A filter has an average flow rate of 2,250 GPM. How long, in hours, will the filter need to run to produce 730,000 gallons of filtered water?
Flow Rate (GPM) =
Filter run time (min) =
Filter run time (min) =

## Slide 21: Gravity Filtration
Most common – conventional and dual media
All washed with full fluidization (bed expansion)

## Slide 22: Single Vs. Dual Media Gradation

## Slide 23: Adsorption & Absorption
Absorption
One substance, such as a solid or liquid, takes up another substance, such as a liquid or gas, through minute pores or spaces between its molecules.
Example: Water takes up carbon dioxide by absorption.
Adsorption
Molecules, such as a gas or a liquid, collect on the surface of another substance, such as a solid.
The molecules are attracted to the surface
Example: Carbon filtration adsorbs contaminants.
Adsorption
Absorption

## Slide 24
Adsorption –molecules collect on the surface of activated charcoal

## Slide 25: Adsorption of Particles
Physical factors affecting adsorption:
  Filter grain size
  Floc particle size
  Adhesive characteristics of the floc
  Shear strength resistance of the floc
Chemical factors affecting adsorption:
  Electrochemical forces
  Molecular cohesive forces between particles (van der Waals forces)
Notes: Van der Walls - weak, short-range electrostatic attractive forces between uncharged molecules, arising from the interaction of permanent or transient electric dipole moments.

## Slide 26: Filtration Mechanisms
Zeta Potential
  Magnitude of electrostatic repulsion between similarly charged particles
  More coagulation = Zeta potential closer to zero
Primary mechanism –particle destabilization (charge neutralization)
  Majority of suspended particles are negatively charged
  Coagulants and cationic polymers - neutralize
  Coagulation and filtration are interrelated
Removal by floc interaction - adsorption
Notes: The zeta potential is a key indicator of the stability of colloidal dispersions. The magnitude of the zeta potential indicates the degree of electrostatic repulsion between adjacent, similarly charged particles in a dispersion. For molecules and particles that are small enough, a high zeta potential will confer stability, i.e., the solution or dispersion will resist aggregation.

## Slide 27: NOM removal

## Slide 28: Filtration Mechanisms
Particle transport (breakthrough)
Mechanisms – physical and chemical
  Adsorption of particles on media surface
Filter run time
  Filtrate quality
  Net plant production
Notes: Particle transport in porous media is conventionally studied using so-called breakthrough curve experiments, based on the analysis of particle concentration at the inlet and outlet of porous media, showing the elution concentration as a function of volumetric throughput

## Slide 29: Filter Sand Characteristics
Effective Size (mm)
Referred to as D10
Size of screen opening where 90% of media is retained and 10% passes
Uniformity Coefficient
Numeric estimate of how sand is graded
Dimensionless
Uc = D60/D10
Uc above 4 = clogging

## Slide 30: Replacement Media

## Slide 31: GRAVITY FLOW SLOW SAND FILTRATION

## Slide 32: Slow Sand Filtration
Pretreatment:
  Roughing filter or sedimentation
  No chemicals or disinfectants
Physical processes: sedimentation, adsorption, straining
Microbiological process (biological mat): oxidation of organics

## Slide 33: Slow Sand Filter
HLR 0.05 – 0.13 gpm/ft2
3 to 5 feet of very fine, washed sand
  0.2 mm effective size
3 to 5 feet of water depth over the sand
Filter run time
  2 to 3 months
Filtration termination criteria
  When outlet chamber water level is near the top of the filter media

## Slide 35: Biological Mat
Surface layer develops a zoological biofilm (Schmutzdecke)
Microorganisms metabolize organic matter
  Advantage - Disinfection Byproduct (DBP) reduction
  Disadvantage – cold temps may decrease activity
Microorganisms and organic matter - must be present in sufficient quantities in source water
Growth occurs principally at the surface of the filter bed

## Slide 36: Slow Sand Cleaning
Upon filter run termination, about one inch of filter media is removed – Schmutzdecke and some sand is removed
Schmutzdecke must reform (filter ripening) before effective filtration is resumed
Ripening may take weeks
Dependent on type and concentration of source water bacteria and nutrients for metabolism

## Slide 37: Slow Sand Capabilities
Produces high quality water from applied water of low turbidity and low bacteria count
Demonstrated > 4.0-log removal of Giardia cysts and Cryptosporidium oocysts
Recognized as conventional treatment
Credited in LT2ESWTR with 3.0-log Cryptosporidium removal as a standalone barrier
Capable of meeting these regulatory limits:
  Turbidity ≤ 1 NTU in at least 95% monthly samples
  Turbidity of filtered water (at no time) < 5 NTU
Notes: Long Term 2 Enhanced Surface Water Treatment Rule

## Slide 38: GRAVITY FLOW RAPID AND HIGH-RATE FILTRATION

## Slide 39: Rapid Rate Operational Characteristics
Filtration rate 1 -2 gal/min/ft2
Usually 30 inches of single media
Minimum 3 ft of water depth over the media
Floc penetration of 2 to 4 inches
  Little depth → head loss inc. rapidly and filter runs are short
  Excessive depth → particle breakthrough

## Slide 40: High-Rate Filtration
Conventional filtration rate ~4 gal/min/ft2
Same 30 inches of filter media
  12 inches sand
  18 inches anthracite on top
  1.0 to 1.4 mm effective size anthracite
Very efficient particle removal
Longer filter runs

## Slide 41: Rapid Rate Gravity Filtration

## Slide 42: Filter Piping
Surface Wash
Backwash Water
Influent Water
Filter to Waste
Notes: Rewash – Filter-to-waste, or rewash, usually has a duration of 15-30 minutes. This allows the initial
particle/turbidity spike to be wasted before placing the filter online. For a well-conditioned filter, the
initial turbidity spike should pass within the first 15 minutes. Ideally, the filter should not be placed
online until the rewash turbidity is at or below 0.1 NTU.

## Slide 43: Slow vs. High/Rapid Rate Filtration
 | Slow Filtration | High/ Rapid Rate Filtration
Pre -Treatment | Treatment for raw water not required | Requires coagulation, flocculation, and sedimentation
Size/Footprint | Large | Small
Rate of Filtration | Small capacity | Large capacity
Flexibility | Low | High
Cost for Construction | Low | High
Skilled Operations | Maybe | Absolutely
Cleaning | Backwash every 1 – 3 months | Backwash every few days

## Slide 44: FILTER OPERATIONS FLOW CONTROL

## Slide 45: Hydraulic Loading Rate
Ratio of flow divided the surface area (gpm/ft2)
Maintaining constant flow (hydraulic grade line) reduces possibility of filter breakthrough
4 Main Methods:
  Effluent rate of flow
  Influent flow split
  Constant level
  Declining rate

## Slide 46: Effluent rate of flow
Controls the rate of treatment through a cell on the filter’s effluent
Basic components:
  Flow-sensing device
  Rate controller
  Actuated valve

## Slide 47: Effluent rate of flow
Pros
  Flow rate is held constant at the set point despite fluctuations in head loss through the system
  Constant treatment rate prevents captured solids released within the filter (breakthrough)
Cons
  Require the most operator attention to calibrate

## Slide 48: Influent Rate Split
Adjustable weir positioned at the entrance of each filter
Inlet weirs are adjustable to be positioned at required elevations to obtain uniform flow splitting
Basic Components:
  Influent control valve
  Effluent hydraulic
  control valve

## Slide 49: Influent Rate Split
Pros
  If filter is removed from service, influent flow to the filter cells is automatically divided among the remaining filters in operation
  Weirs are located so easy for visual inspection to ensure debris hasn’t fouled the weirs
Cons
  Can exceed the filter designed HLR if incoming flow exceeds the available online filter area

## Slide 50: Constant Level Control
Uses level-sensing device in each filter to communicate with a control valve in the effluent line
Compares current conditions with desired set points and works in conjunction with the control valve to align the two conditions
Basic Components:
  Actuated valve
  Level sensor

## Slide 51: Constant Level Control
Pros
  Eliminates potential media surface scouring – filter water level is always located well above the media surface
Cons
  Can have potential flow stabilization issues
  Operator is not able to visually see head loss building in the filter

## Slide 52: Declining Rate Filtration
Oldest and simplest method of filter control
Influent water enters the filter below the cell water level
Water flows freely into the cells – all filter cells are fluidly connected through the influent system
Flow through a filter based on the head loss in a filter cell – filter that has been running the longest is backwashed

## Slide 53: Declining Rate Filtration
Pros
  Minimal control component requirements - easy to operate
  Handles variable influent flow rates better than most other control systems - variations are spread out among more filters
Cons
  Risk of turbidity breakthrough in clean cells if not limited to a maximum rate
  Individual filter monitoring is difficult

## Slide 54: FILTER OPERATIONS UNDERDRAIN SYSTEMS

## Slide 55: Underdrains
Collect filtrate (clean water)
Distribute backwash water
Equal distribution is key

## Slide 56: Media Bed Expansion
Bed expansion – effect during backwash when filter media separates and rises
Adequate bed expansion = critical to effective backwash
  Poor filter performance (shortened run times)
  Sensitivity to hydraulic surges
  Reduced finished water quality
Usually expressed as % increase in bed depth

## Slide 57: Fluidizing
Trapped dirt causes dead spots (mud balls)
Can observe low turbidity at end of backwash
Media moves and collides
Scrubbing and separation action

## Slide 58: Design Issues
Headloss through underdrains – uneven distribution/collection of water
Headloss through manifold vs. system
  Orifice openings (most hL)
  Filter media
  Gravel
  Elevation head
hL can range from 10 -15 FT

## Slide 59: Design Issues
Media wash out
Backwash rate too high
Dead spots – uneven air distribution
Air entrainment

## Slide 60: FILTER OPERATIONS BACKWASHING

## Slide 61: Backwash Objective
Removal of trapped and attached particles
Backwash rate (gpm/ft2) expands and agitates filter bed
  Velocity – energy to expand and agitate
  Sphericity - measure of how spherical (round) an object is – energy transfer
  Viscosity (temperature) – energy transfer
Surface wash and air scour assisted

## Slide 62: Backwash Rate
Increasing backwash rate needed
Larger grain, less uniform

## Slide 63: Backwash Rise Rate
Volume of water flowing upward through a unit of filter surface area
Measured as rise of water in inches per minute
Rates typically between 20 and 35 inches per minute

## Slide 64: Backwash Rise Rate
A filter has a backwash rate of 21 GPM per FT2. What is the backwash rise rate in inches per minute?
33.6 in/min

## Slide 65: Backwash Water Volume
A 15 FT x 20 FT filter has a backwash rate of 16 gallons per square foot per minute (gal/ft2/min), and the backwash cycle is, on average, 10-minutes long. The filter media is 30-inches deep. Calculate the amount of water, in gallons, required for each backwash.

## Slide 66: Backwash Water Volume
Area of filter = 15 FT x 20 FT = 300 FT2
Volume of water used per FT2 of filter =
16 gal/FT2/min x 10 min = 160 gal/FT2
Gallons required for backwash =
160 gal/FT2 x 300 FT2 = 48,000 gal

## Slide 67: Backwash Pumping
A filter is 18 ft long and 8 ft wide. The desired backwash rate is 20 gpm/FT2. Find the backwash pumping rate, in GPM, that will be required.

## Slide 68: Backwash Pumping
Pumping rate, gpm =
Backwash rate, gpm/FT2 x Filter area, FT2
Pumping rate, gpm =
20 gpm/FT2 x (18 FT x 8 FT)
Pumping rate, gpm = 2,880 gpm

## Slide 69: Produced Water
During an average day, 12.4 MGD was produced using 6 filters. If 63,000 gallons of the finished water was used for backwashing Filter #3, what percent of the finished water was used for backwashing that filter?

## Slide 70: Produced Water

## Slide 71: Backwash Sequence
1
Close influent
2
Draw down water level
3
Surface wash or air scour
(1-2 mins)
4
Stop surface wash or air scour
5
Start backwash flow slowly
(expels air)
6
Full backwash
(fluidize)
7
Slowly reduce backwash rate

## Slide 72: Surface Wash and Air Assisted

## Slide 73: Observing Backwash Sequence
Bed expansion and media freeboard
  Media loss (some is normal)
Uneven distribution of the backwash water
Mud balls (heavier)
Sand boils while backwashing – separation of gravel (backwash valve opened too quickly)

## Slide 74: Placing Clean Filter In Service
Slowly refill filter box
Open rewash/filter to waste valve
Rewash/filter to waste facilitates filter curing
  Coagulant coating the media
  Floc particles beginning to be adsorbed
Rewash until filtered water turbidity is ≤ 0.1 NTU
To effectively and economically rewash to low NTU levels
  Must know and control rewash rate
  Filter curing can be enhanced by dosing backwash water with coagulant

## Slide 75: Backwash Video

## Slide 76: QUESTIONS? Contact info: Caleb Taylor, P.E. ctaylor@nrvwater.org 540-639-2575
Thank you!