## Slide 1: Coagulation and Flocculation Principles – Part II
Bruce Utne, butne@nnva.gov
John Hanchak Jr., jhanchak@nnva.gov
Newport News Waterworks

## Slide 2: Presentation Objectives
Review Coagulation Principles
Factors Impacting Coagulation
Coagulation Evaluation Tools
Coagulation Optimization (example)
Notes: Edited-6/24/19

## Slide 3: Credits
John Hanchak, Sr.
Dr. Bill Knocke, VT
Dr. Jim Edzwald, UMass
Also draw heavily from:
AWWA Water Supply Operations texts
AWWA Manual of Water Supply Practices, M37

## Slide 4: Key Points:
pH should be in _______ range for max floc production (aluminum based coagulants).
Removal of NOM increases at _____ pH for both aluminum and iron based coagulants.
Notes: 6.0 – 6.5 range
Lower pH

## Slide 5: Coagulation
Purpose of Coagulation:
  To pre-treat or condition contaminants (suspended particles and dissolved organic material) so they can be more easily removed in downstream processes.
Challenges:
Particles (especially small ones) tend to be stable (i.e. do not want to come together);
Dissolved organic material will pass right through sedimentation and filtration processes.
Notes: Coagulation chemicals are able to bring suspended particles and dissolved organic material together. The chemistry is complicated, but we generally understand that at least four things are happening at the same time.

## Slide 6: The challenge: Particle stability
Natural particles in the colloidal size range do not settle quickly enough to be removed in sedimentation basins.
In addition, most particles have a net negative surface charge.
  Like charges repel each other  particles do not want to stick to each other or to filter media  Therefore, remain in solution:
  “Stable”
Notes: Colloidal = very small

## Slide 7: The solution: Destabilization
To overcome or neutralize the repelling forces between particles, we add chemicals known as coagulants
Commonly, tri-valent metal salts of Aluminum or Iron such as:
  Aluminum Sulfate, Al2(SO4)3 . 14H2O
  Polyaluminum Chloride
  Ferric Sulfate, Fe2(SO4)3
  Ferric Chloride, FeCl3
Al+3  Al(OH)3
Fe+2 or Fe+3  FeCl3 or Fe2(SO4)3
Notes: Valence refers to the charge of the atom or molecule and is related to the balance of electrons and protons.
When neutral, atoms have an equal number of protons and electrons; many atoms will either give up electrons or take extra electrons giving them either a positive or negative charge. In this case, metals that have given up three electrons so they carry a +3 charge.
“Tri-valent metals”; i.e. will give up three electrons and therefore have a +3 ionic charge.
Anybody use a coagulant other than these?

## Slide 8: More Definitions:
Due to their small size and/or repelling forces, particles that remain in suspension are referred to as being stable.
Destabilization refers to the process of reducing the repelling forces between particles and organic material so that particles/organic matter will agglomerate or gather together into larger floc particles.

## Slide 9: Coagulation
(From AWWA Water Supply Operations):
Coagulation is a chemical process involving reactions with both particles and natural organic material. These reactions cause very small suspended particles to attract one another and form larger particles.
This is accomplished by the addition of a chemical (referred to as a coagulant) that neutralizes the electrostatic charges on particles which cause them to repel each other.
Notes: A “Process” in which treatment chemicals are added to water causing the reduction or elimination of the REPLUSIVE forces that exist between particles.
Occurs when electrokinetic (-) charge is reduced or eliminated

## Slide 10: Flocculation
(From AWWA Water Supply Operations):
Water treatment process following coagulation that uses gentle stirring to bring suspended particles together so they will form larger, more settleable clumps called floc.
The agglomeration of destabilized floc particles and colloids into larger floc masses.
Notes: WSO definition of Flocculation: the water treatment process, following coagulation, that uses gentle stirring to bring suspended particles together so that they will form larger, more settleable clumps called floc.

## Slide 11: Flocculation (continued)
Is a physical step (process) during which the size of particles are increased due to collision with and attachment to other particles.
Therefore,
Must have an energy input, either hydraulic or mechanical, to cause collisions between particles.
Notes: WSO definition of Flocculation: the water treatment process, following coagulation, that uses gentle stirring to bring suspended particles together so that they will form larger, more settleable clumps called floc.

## Slide 12: Coagulation / Flocculation
Quick Summary:
Coagulation is a chemical process involving the addition of chemicals to destabilize particles and organic material.
Flocculation is a physical process involving the collision and growth of small particles into larger particles.
  … these are SEPARATE processes!
Notes: Have students write the following in the margins of their notebooks!
Purpose of Coagulation is to destabilize particles (so they will come together, form larger floc particles and be removed by clarification and/or filtration.)
Purpose of Flocculation is to build floc particles of optimum size, density, and strength
Next few slides focus on particles and NOM.

## Slide 13: Particles (turbidity)
Turbidity: a physical characteristic of water that makes water appear cloudy.
  Turbidity is caused by the presence of suspended material (i.e. particles).
  Generally 0.01 to 100 μm in size.
  Larger particles easily settle out
  Smaller, colloidal fraction (0.01 to 5 μm) have extremely slow settling velocities and can easily pass through media filters (unless they are properly “conditioned”).
Notes: (I like) Colloid: an extremely small particle suspended in water which cannot be removed by plain sedimentation or filtration without coagulation.
Colloids are generally not filtered out in the suspended solids test, but are not dissolved.
See WSO 4th ed. P. 47 for Suspended, colloidal, dissolved solids
Settleable vs. non-settleable solids
Suspended, colloidal, dissolved solids

## Slide 14: Particles (continued)
Size and surface properties are two of the most important characteristics of particles related to their removal by coagulation and filtration.
Particle types:
  Organic
  Inorganic
  Biological
Why so important that we remove particles from water?
  Microbes are particles!
  Particles may harbor or shield microbes from disinfectants and therefore reduce the effectiveness of the disinfectants.

## Slide 15: Natural Organic Matter
Comes from the degradation (decomposition) of vegetation, run-off from organic soils, and biological activity. (aka: humic substances)
In itself, not a health concern, however, elevated levels produce discoloration and taste/odor issues.
Can react with chlorine to form a variety of disinfection by-products, some of which are regulated; e.g. THMs and HAAs
Notes: NOM: vegetative decay, run-off from organic soils, and biological activity
THM = trihalomethanes
HAA = halo acetic acids
Humic substances (HS) are a category of naturally occurring organic compounds that arise from the decomposition and transformation of plant, animal, and microbial residues (MacCarthy, 2001)
Test prep #29, 44 (?)

## Slide 16: Natural Organic Matter (cont.)
NOM referred to as DBP precursor material.
Measured as Total Organic Carbon (TOC)
- Dissolved fraction (DOC)
Generally large molecules containing many different types of functional groups.
Charge on functional groups affected by pH.
Notes: DBP = disinfection by-products
Need to explain Humic and Fulvic substances?
Hydrophobic and hydrophyllic (sp?)
Also consider showing relationship between TOC and DOC  most NOM is dissolved. Coagulation converts dissolved NOM to a solid form that can be removed by clarifiers and filters.

## Slide 17: Good Coagulation is ESSENTIAL!
Coagulation affects:
  Particle formation during flocculation
  Particle/NOM removal in clarification processes (sedimentation or flotation)
  Particle capture/removal by granular media or membrane filters (ripening times and breakthrough)
Notes: Water treatment plants need good coagulation!

## Slide 18: So, we have to get it right!
Each water is different.
  River, lake/reservoir, aquifer
  Watershed, upstream activity
  Turbidity, NOM
Water quality changes with each season (temperature, turn-over) and precipitation/ storm events.
Notes: Q: Ask students about their source water and what are typical ranges of raw water turbidity and TOC?
Write some of the numbers on white board or easel. (Refer back to TOC for Enhance Coagulation requirements)
Will also be asking students later what controls their coagulant dose, turbidity or TOC/NOM

## Slide 19: Seasonal Changes in Source Water
Chart: TOC, mg/L
| 42009 | 42016 | 42024 | 42030 | 42037 | 42044 | 42054 | 42058 | 42065 | 42072 | 42079 | 42086 | 42093 | 42100 | 42107 | 42114 | 42121 | 42128 | 42135 | 42142 | 42150 | 42157 | 42164 | 42171 | 42178 | 42185 | 42192 | 42199 | 42206 | 42214 | 42220 | 42227 | 42234 | 42241 | 42248 | 42256 | 42261 | 42269 | 42276 | 42284 | 42290 | 42297 | 42304 | 42311 | 42318 | 42325 | 42332 | 42339 | 42346 | 42353 | 42360
Chickahominy River | 6.2 | 6.78 | 6.22 | 6.22 | 7.09 | 5.49 | 5.21 | 5.37 | 4.82 | 4.26 | 5.8 | 6.92 | 7.77 | 7.7 | 8.12 | 10.06 | 13.2 | 10.5 | 10.26 | 10.75 | 11.63 | 10.9 | 8.48 | 9.78 | 11.64 | 10.79 | 10.03 | 11.9 | 11.7 | 10.64 | 10.65 | 9.34 | 8.36 | 8.05 | 8.37 | 7.97 | 8.2 | 7.56 | 7.8 | 8.61 | 10.88 | 10.7 | 10.01 | 9.66 | 8.56 | 11.45 | 10.24 | 9.11 | 7.76 | 7.34 | 6.76
Diascund Creek Reservoir | 4.61 | 4.52 | 6.28 | 4.43 | 4.63 | 4.31 | 4.42 | 4.54 | 4.68 | 5.17 | 6.78 | 5.22 | 5.34 | 3.59 | 3.47 | 5.66 | 6.01 | 4.41 | 6.47 | 6.99 | 5.01 | 7.09 | 7.07 | 6.1 | 7.19 | 6.91 | 7.3 | 7.58 | 7.38 | 7.25 | 7.51 | 7.44 | 7.91 | 7.85 | 7.62 | 7.75 | 7.55 | 7.72 | 9.15 | 9.14 | 7.42 | 8.21 | 6.92 | 7.34 | 7.15 | 7.14 | 5.64 | 5.76 | 5.88
Little Creek Reservoir | 4.28 | 3.25 | 3.71 | 3.34 | 3.72 | 3.68 | 3.64 | 3.69 | 3.68 | 3.22 | 4.66 | 3.85 | 3.94 | 4.09 | 3.98 | 4.58 | 5.62 | 3.9 | 4.26 | 3.98 | 3.65 | 3.9 | 4.23 | 4.28 | 3.88 | 3.58 | 3.64 | 3.51 | 3.82 | 3.54 | 7.35 | 5.04 | 4.26 | 3.36 | 3.95 | 3.56 | 3.54 | 3.52 | 3.66 | 3.66 | 3.73 | 4.18 | 3.87 | 3.02 | 3.39 | 3.75 | 3.4 | 2.75 | 3.21 | 2.71

## Slide 20: Regulatory Requirements: Particles
LT1ESWTR: Surface water plants (or ground water under the direct influence of surface water) using granular media filtration must achieve:
    <0.3 NTU in at least 95% of the combined filter effluent compliance samples each month (collected every 4 hrs).
    <1 NTU combined filter effluent at any time.

## Slide 21: Regulatory Requirements: NOM
Stage 1 D/DBP: Surface water plants (or GWUDISW) using conventional treatment must remove a specified amount of NOM measured as total organic carbon (TOC).
  aka: Enhanced Coagulation Rule
  Compliance determined by amount of TOC removal
  Required TOC removal based on source water TOC and alkalinity.
Notes: Add in information regarding SUVA
Test prep: enhanced coagulation requirements of the D/DBP rule #47, p. 120

## Slide 22: Stage 1 D/DBP Rule:
Required Percent Removal of TOC based on source water TOC and alkalinity |  |  | 
 | Alkalinity |  | 
TOC (mg/L) | 0-60 mg/L | 60-120 mg/L | >120 mg/L
less than 2.0 mg/L | no action | no action | no action
2.0 to <4.0 mg/L | 35 | 25 | 15
4.0 to <8.0 mg/L | 45 | 35 | 25
greater than 8.0 mg/L | 50 | 40 | 30
Notes: Q: Where is your utility? Is your utility always in the same box, or does your TOC removal requirement change occasionally?
TOC removal is used to determine compliance with the {enhanced coagulation} requirements of the D/DBP rule #47, p. 120

## Slide 23: TOC Removal Requirements: Observations / Trends
As raw water TOC increases, the required level of TOC removal increases
  Why? A: Generally, the more TOC to start, the easier it is to remove.
For a particular level of TOC, the required level of TOC removal decreases as alkalinity increases.
  Why? A: Alkalinity resists pH changes; TOC is easier to remove at lower pH (5 – 6). Therefore, high alkalinity waters may require excessive chemical doses to achieve desired pH for NOM removal.
Water systems can be exempt from Stage 1 and 2 D/DBP rule if the source water TOC is < 2.0 mg/L (calculated on running annual average)
Notes: Reference Test prep #189, p. 86 re: TOC removal requirements
See WSO 4th edition, Table 4-4, p. 54 and new WSO Grade 2, p. 77-78 including target pH values, Table 3-3.
See Test prep #23, p. 117 regarding exemption requirements.
Test prep: Water that is highly colored with organic material requires a lower pH for coagulation; therefore, acid addition before coagulation may be necessary. #53, p. 66

## Slide 24: Optimizing Coagulation
Maximize:
  Removal of particles (turbidity) and NOM (color, DBP precursors) by downstream processes (clarification or filtration)
Minimize:
  Residual coagulant in finished water
  Sludge production
  Operating Costs (chemicals, sludge processing, production efficiency)
Notes: Mention concept of diminishing returns in regards to NOM removal. (Show some data; perhaps do set of jars and measure DOC/UV254)

## Slide 25: Optimizing Coagulation
  A coagulation process that is optimized for both particle and NOM removal is known as:
  Enhanced Coagulation (EC)
Notes: Before the D/DBP rule, focus was mainly on particle removal. D/DBP Rule brought more focus on removal of DBP precursors, hence it is referred to as the enhanced coagulation rule.
Which one drives the coagulant dose: turbidity or organic material? Test prep: (#88, p. 71) Turbidity and organic determine the amount of coagulant needed.

## Slide 26: Coagulation Mechanisms
Q: How do coagulants bring particles together and remove dissolved organic material?
 Need to understand what happens when coagulants are added to water….
Notes: To provide a good answer to this question, we need ……

## Slide 27: Coagulation Chemistry
When coagulants are added to water, they dissociate (separate into charged ions) and hydrolyze (react with water) to form a variety of charged coagulant species that interact with particles and NOM.
Al2(SO4)3 14H2O  Al+3, SO4-2  Al(OH)+2  Al(OH)2+1  Al(OH)3  Al(OH)4-1
H2O  H+1 OH-1
H+1 OH-1
H+1 OH-1
H+1 OH-1
Hydrogen ions go into solution lowering the pH and consuming alkalinity
Notes: This is simplified.
Perhaps better to say, “reacts with alkalinity”
Either HCO3 or OH depending on relative concentration of each
Hydrolysis: the chemical breakdown of a compound due to reaction with water. (Google)

## Slide 28: Aluminum Chemistry
Aluminum reacts with water to quickly form a variety of charged chemical species.
Charged coagulant species react with negativiely charged particles and NOM to neutralize them or form insoluble Aluminum-NOM complexes.
The relative concentration of each specie depends on the solution pH
  At pH < 6.5, mostly positively charged
  Above pH 6.5, becomes more negatively charged
At aluminum concentrations above solubility, aluminum hydroxide floc (precipitate) is formed. Particles may get enmeshed in floc or NOM may adsorb to floc surface.
For maximum floc formation, desire pH ~6.0-6.5 for warm waters (slightly higher pH for colder temps).
Figure borrowed from Knocke, Edzwald
Notes: For bottom graph, consider Aluminum as mg/L Alum vs. mg/L Aluminum vs. moles/liter Aluminum.
As alum naturally lowers the pH of the water, required dose may result in favorable pH conditions for forming Aluminum Hydroxide floc. If alkalinity too high or low, may need to adjust pH.
pH of minimum solubility increases as water temperatures drop.
For maximum floc formation, want pH at or near point of minimum solubility.

## Slide 29: Coagulation Mechanisms
Enmeshment in aluminum hydroxide Al(OH)3 floc particles, a.k.a “sweep floc”
NOM adsorption to surface of floc particles
Charge neutralization
Complexation or direct precipitation with NOM
Adsorption: The adhesion of atoms, ions, or molecules in a gaseous, liquid or dissolved solid state to a surface.
Notes: Do not confuse adsorption with absorption (like a sponge/paper towel)

## Slide 30: Conceptual View of Coagulation Mechanisms
Alkalinity Consumption
Al+3, SO4-2
Al+3, AlOH+2, Al(OH)4-1
Al+3, AlOH+2
Al(OH)3 (amorphous)
Alum
Colloids
NOM
Colloids
NOM
(2) Adsorption
(3) Charge Neutralization
(4) Complexation/ Precipitation
(1) Enmeshment
Hydrolysis
H+
Active Coagulant Species
Contaminant
Mechanism
Coagulant
Recreated from Coagulation 101, David J. Pernitsky, Ph.D.
Al(OH)2+
Al(OH)2+
Magnitude of positive surface charge on Al(OH)3 solids increases as pH decreases. Therefore, adsorption of NOM onto floc particles increases at lower pH
Notes: All four mechanisms in play, however, at higher alum doses, sweep floc (enmeshment and adsorption) will be major players.
Al(OH)3 in equilibrium with other coagulant species. Magnitude of positive surface charge on Al(OH)3 solids is dependent on pH. More positive with decreasing pH. Therefore adsorption of NOM increases with decreasing pH.

## Slide 31: Ferric Coagulation
Similar reactions with iron, Fe+3  Fe(OH)3 (solid)
However, compared to Aluminum,
  Iron is much less soluble than aluminum
  Iron is effective over a wider range of pH (5 <pH< low 8s)
  Optimum pH for TOC removal with iron is lower than for alum
    Waters with moderate to high TOC, recommend pH = 5.0 to 5.5
  Temperature does not impact coagulation with iron as much as alum.
Notes: Test prep!
One advantage of ferric sulfate over alum is that it is effective over a wider pH range (#51, p. 66)
The correct chemical formula for hydrated ferric sulfate is Fe2(SO4)3 – 3H2O (question reference?)

## Slide 32: Polyaluminum Chloride (PACl) Chemistry
Aluminum based, therefore similar hydrolysis products as alum; however, predominant species is polymeric (more than one aluminum atom in molecule):
Al13O4(OH)24(H2O)12+7
Key point: pH of minimum solubility is higher for PACl than alum. This allows for coagulation at higher pH.
PACls are formulated to consume less alkalinity.
from Coagulation 101, David J. Pernitsky, Ph.D.
Notes: See also Knocke presentation for additional information on PACl.

## Slide 33: Let’s Take a Break

## Slide 34: Water Treatment Math Practice Coagulation
What is the required feed rate for alum in mL/min for a dose of 40 mg/L and a plant flow of 10 mgd?
Assumptions:
Product is 48.5% as dry alum
Product has a specific gravity of 1.32
Notes: What do we need to solve this problem?

## Slide 35: Math Practice: Coagulation
Feed rate (lb/day) = Flow (mgd) x Dose (mg/L) x 8.34
10 mgd x 40 mg/L x 8.34 = 3,336 lb/day (as alum)
Tricky part: How convert lb/day to mL/min?
Converting days to minutes not too bad.
Converting lbs to mL?
 need solution strength!
With information given, we can calculate lb (dry alum)/gal:
If liquid alum has specific gravity of 1.32, then 1 gallon of liquid alum weighs 1.32 times more than a gallon of water.
Q: What is the required feed rate for alum in mL/min for a dose of 40 mg/L and a plant flow of 10 mgd?
Assumptions:
Product is 48.5% as dry alum
Product has a specific gravity of 1.32

## Slide 36: Math Practice: Coagulation
With information given, we can calculate lb (dry alum)/gal:
If liquid alum weighs 11.0 lb / gal and the liquid product is 48.5% dry alum, then:
= 1,642 mL/min
Q: What is the required feed rate for alum in mL/min for a dose of 40 mg/L and a plant flow of 10 mgd?
Assumptions:
Product is 48.5% as dry alum
Product has a specific gravity of 1.32
Feed rate: 3,336 lb/day as dry alum

## Slide 37: What controls coagulant dose?
Particles or NOM?
Answer: NOM controls coagulant dose for most waters.
The charge density of the NOM functional groups is typically 10 to 100 times greater than the charge density of inorganic particles. Therefore, NOM exerts a much greater coagulant demand.
Notes: Test prep: #88, p. 7 Both turbidity and organic material determine the amount of coagulant needed.
Perhaps show how nature of TOC changes TOC vs. UV chart; Introduce SUVA? Show also how SUVA varies with TOC.

## Slide 38: Natural Organic Matter (cont.)
NOM referred to as DBP precursor material.
Measured as Total Organic Carbon (TOC)
- Dissolved fraction (DOC)
Generally large molecules containing many different types of functional groups.
Charge on functional groups affected by pH.
Notes: DBP = disinfection by-products
Need to explain Humic and Fulvic substances?
Hydrophobic and hydrophyllic (sp?)
Also consider showing relationship between TOC and DOC  most NOM is dissolved. Coagulation converts dissolved NOM to a solid form that can be removed by clarifiers and filters.

## Slide 39: NOM (a little deeper)
Comes from the degradation (decomposition) of vegetative material, run-off from organic soils, and biological activity.   NOM from different sources will have different characteristics.
Coagulation more effectively removes NOM of high and intermediate molecular weight.
(Humic vs. Fulvic material)
Notes: Humic typically larger molecular weight fraction; Fulvic typically lower molecular weight.

## Slide 40: Specific Ultraviolet Absorbance (SUVA)
Fractionating NOM is difficult
 SUVA useful as a simple tool to assess the nature of NOM and likelihood that it can be removed through coagulation.
SUVA is a measure or indicator of the type of NOM present.
Notes: Define “Fractionating”

## Slide 41: SUVA
SUVA = UV254 absorbance (cm-1) X 100
DOC (mg/L)
SUVA increases as UV absorbance increases and DOC decreases.
** NOM with high SUVA values is easier to remove via coagulation than low SUVA.

## Slide 42: Relationship between DOC and UV254
Chart: Lee Hall Reservoir
| 5.5 | 5.68 | 5.77 | 5.68 | 5.93 | 5.76 | 5.63 | 5.4 | 5.26 | 5.29 | 5.49 | 5.54 | 5.76 | 6.21 | 5.61 | 5.53 | 5.63 | 5.73 | 6.04 | 5.8 | 6.62 | 7.29 | 7.32 | 7.24 | 7.07 | 6.96 | 6.96 | 6.52 | 6.62 | 6.93 | 7.57 | 7.3 | 7.13 | 6.53 | 6.73 | 5.96 | 5.75 | 5.52 | 6.47 | 6.58 | 7.3 | 7.94 | 7.94 | 8.15 | 7.19 | 7.61 | 7.48 | 7.41 | 7.37 | 6.95 | 6.66
Raw UV254 Filt | 0.144 | 0.147 | 0.162 | 0.147 | 0.161 | 0.154 | 0.141 | 0.155 | 0.143 | 0.152 | 0.153 | 0.177 | 0.182 | 0.178 | 0.172 | 0.163 | 0.174 | 0.178 | 0.166 | 0.158 | 0.209 | 0.221 | 0.257 | 0.226 | 0.208 | 0.21 | 0.2 | 0.186 | 0.189 | 0.213 | 0.232 | 0.243 | 0.213 | 0.188 | 0.19 | 0.129 | 0.152 | 0.142 | 0.158 | 0.201 | 0.235 | 0.247 | 0.246 | 0.244 | 0.234 | 0.245 | 0.214 | 0.244 | 0.257 | 0.232 | 0.224
SUVA = 4.17
Careful! SUVA is calculated with DOC not TOC
Notes: Shows correlation between raw water DOC and UV254. (Why DOC and not TOC? What is difference?)
Slope of line x 100 = SUVA
The slope of the line is our average or “normal” SUVA. Where individual data points fall above the line, then NOM will be a little easier to remove than “normal”. And vice versa

## Slide 43: Expected DOC (TOC) removal
SUVA | Coagulation | DOC Removal
< 2 | NOM has little influence; poor DOC removal | < 25% with Alum; potentially higher with Ferric
2 – 4 | NOM has influence on coagulant dose; DOC removal fair to good | 25 – 50% with Alum; potentially higher with Ferric
> 4 | NOM controls coagulant dose; Good DOC removal | > 50% with Alum; potentially higher with Ferric
From Manual of Water Supply Practices, M37 (AWWA)
Notes: For waters with SUVA greater than 2, the amount of NOM typically exerts a greater coagulant demand than the amount of particles. Coagulant demand (and dose) increase with increasing levels of NOM (TOC/DOC).
Which one drives the coagulant dose: turbidity or organic material? Test prep: (#88, p. 71) Turbidity and organic determine the amount of coagulant needed.

## Slide 44: Test Prep:
Q: Water that is highly colored with organic material requires a _______ pH for coagulation; therefore, _______ before _______ may be necessary.
Lower, acid addition, flocculation
Higher, alkalinity addition, flocculation
Lower, acid addition, coagulation
Higher, alkalinity addition, coagulation
Answer: c. Lower, acid addition, coagulation
Water Operator Certification Exam Prep: page 66, #53

## Slide 45: Test Prep:
Q: The specific ultraviolet absorbance (SUVA) is calculated using the absorbance of UV light at 254 nm _______ the concentration of _______.
Multiplied by, TOC
Divided by, TOC
Multiplied by, dissolved organic carbon
Divided by, dissolved organic carbon
Answer: d. Divided by, dissolved organic carbon
Water Operator Certification Exam Prep: page 99, #58

## Slide 46: Factors affecting coagulation

## Slide 47: Factors Affecting Coagulation
pH
Alkalinity and buffer intensity
Temperature
Nature of NOM
Turbidity
Pre-oxidation
Mixing
Notes: This list from WSO texts, but two main factors are:
What chemical(s) you are using!
What DOSE!!
Aside from these two, this list represents other major players (not necessarily in this order)
Will focus on first three this year.
Need to review difference between alkalinity and buffer intensity.

## Slide 48: Factors Affecting Coagulation: pH
pH affects:
  surface charge of colloids
  charge of NOM functional groups (better removal at lower pH)
  surface charge of floc particles
  charge and form of dissolved coagulant species
  coagulant solubility!!
Notes: Waters highly colored with organic material require a lower pH for coagulation; therefore, acid addition before coagulation may be necessary. #53, p. 66

## Slide 49: Aluminum Chemistry
Aluminum reacts with water to quickly form a variety of charged chemical species.
The relative concentration of each specie depends on the solution pH
  At pH < 6.5, mostly positively charged
  Above pH 6.5, becomes more negatively charged
Charged coagulant species react with particles and NOM to neutralize them or form Aluminum-NOM complexes.
At aluminum concentrations above solubility, aluminum hydroxide floc (precipitate) is formed. Particles may get enmeshed in floc or NOM may adsorb to floc surface.
For maximum floc formation, desire pH ~6.0-6.5 for warm waters (slightly higher pH for colder temps).
Figure borrowed from Knocke, Edzwald
Aluminum solubility increases as the pH moves away from the low 6’s in both directions.
Therefore, best coagulation performance is generally seen at pH values close to the pH of minimum solubility.  Increases floc formation and minimizes dissolved aluminum residuals.
(Note: pH of minimum aluminum solubility increases slightly as temperature decreases)
Notes: For a given alum dose, floc formation will decrease if pH allowed to drop below 5.5 or increase above 7.0
At colder temperatures, may need to coagulate at slightly higher pH (monitor dissolved aluminum residual)  Table 1-3 in M37 shows pH of minimum solubility of aluminum increasing from 6.0 to 6.2 as temperature decreases from 20 C to 5 C

## Slide 50: Factors Affecting Coagulation: pH
pH of minimum Al solubility ~ 6.0-6.5
pH of minimum Fe solubility ~ 8.5-8.8; however, iron is more effective at lower pH (~5.5) and over a wider pH range than alum.
** iron has a much lower solubility than aluminum, therefore it is acceptable to use it at a pH that is considerably lower than its pH of minimum solubility.
But, why would we coagulate at a pH lower than its pH of minimum solubility?
Notes: WRITE THIS DOWN! Both Alum and Iron coagulants achieve greater NOM (i.e. TOC) removal at lower pH values.

## Slide 51: Closer look at: pH
What happens to pH when add alum or iron coagulants? ….. Why?
pH is a measure the hydrogen ion concentration, [H+] and indicates how acidic or basic a solution is. The pH scale runs from 0 (most acidic) to 14 (most basic)
Anything that increases [H+] is an Acid
Anything that increases [OH-] is a Base
(Anything that decreases [H+] is a Base)
(Anything that decreases [OH-] is an Acid)
If [H+] , then pH
Notes: I think we all know that when we add coagulants to water, the pH will decrease…..
Want to dive a little deeper. Understanding pH will help us understand the role of alkalinity.

## Slide 52: Closer look at: pH
H2O H+ + OH-
pH = -log10[H+]
At pH = 7, [H+] = 10-7 or 0.0000001 moles/L
At pH = 6, [H+] = 10-6 or 0.000001 moles/L
Thus, there are 10x as many H+ ions at pH 6 than pH 7
Notes: Water molecules dissociate into H+ and OH- ions.
Could also measure the [OH-} concentration; at pH 7, there are an equal number of H+ as OH-; therefore neutral

## Slide 53
100
10-8
10-6
10-4
102
10-2
104
106
10-10
1
100
10,000
0.01
0.0001
0.000001
0.00000001
1,000,000
pH = 8
6
4
2
10
0
pH scale indicates [H+] concentration
Acidic
Basic
pH = 7 Neutral
At pH = 7, [H+] = [OH-]  Neutral

## Slide 54: Closer look at: pH
What happens to pH when add alum or iron coagulants? ….. Why?
When add Alum, the [H+] (and pH ) because:
Alum is made with sulfuric acid (H2SO4)  extra [H+]
As Al(OH)3 floc are formed, [OH-] ions are consumed which increases the [H+] relative to [OH-] and causes the pH to decrease.

## Slide 55: HM Changing to Acid Alum, pH change

## Slide 56: Sulfuric Acid Feed: pH drop and CFE improvement
Notes: Lee Hall WTP

## Slide 58: Factors Affecting Coagulation: Alkalinity
Desire lower pH during coagulation to improve NOM removal and increase floc formation, but if the pH drops too far  TROUBLE!
Thus, Alkalinity is very important!
(From WSO) Alkalinity is a measurement of water’s capacity to neutralize an acid.
Notes: Does anyone know what alkalinity is composed of? i.e. what are we really measuring when we measure alkalinity?

## Slide 59: Factors Affecting Coagulation: Alkalinity
Alkalinity = [OH-1] + [HCO3-1] + 2[CO3-2] – [H+]
Hydroxide Bicarbonate Carbonate
When an acid is added, each one of these compounds will combine with a H+ ion and limit the increase of free H+ ions in solution. By limiting the number of H+ ions, these compounds serve to buffer large changes in pH.
Notes: Aside: if not enough OH- available to form aluminum or ferric hydroxide, the bicarbonate ions will give up an OH-, leaving CO2; CO2 is an acid as it combines with water to form H2CO3.
Google: Alkalinity consists of ions that incorporate (acid) protons into their molecules so they are not available as free acid that can lower the pH.
At pH 7, most alkalinity in the form of bicarbonate!

## Slide 61: Factors Affecting Coagulation: Alkalinity
Dangers of exhausting alkalinity
    Little/no floc formation in floc basins
    (no OH- or HCO3- available to form floc)
    Increasing dissolved metal concentration (aluminum, iron)
    Post-filter floc formation (after raise pH back up)
How much alkalinity do coagulants consume?
Notes: Consider reviewing alkalinity here? and showing alum reaction with alkalinity (one equation from zeta-meter paper on everything you want to know...)
Lime is often added to provide alkalinity and facilitate iron precipitation. #54, p. 66
options for increasing alkalinity: lime, soda ash, caustic soda, and sodium bicarbonate.
Lime is cheapest, but more difficult to handle/feed.

## Slide 62: Coagulation Chemistry Reactions
Alum:
Al2(SO4)3 14H2O + 3Ca(HCO3)2
2Al(OH)3 + 3CaSO4 + 6CO2 + 14H2O
Ferric Sulfate:
Fe2(SO4)3 18H2O + 3Ca(HCO3)2
2Fe(OH)3 + 3CaSO4 + 6CO2 + 18H2O
Notes: Aside: if not enough OH- available to form aluminum or ferric hydroxide, the bicarbonate ions will give up an OH-, leaving CO2; CO2 is an acid as it combines with water to form H2CO3.

## Slide 63: Alkalinity consumption per addition of 1 mg/L of Coagulant
1 mg/L coagulant
Alum
Ferric Sulfate
Ferric Chloride
Polyaluminum Chloride (Higher basicity less alkalinity removal)
reduces alkalinity by:
0.5 mg/L as CaCO3
0.35 mg/L as CaCO3
0.92 mg/L as CaCO3
0.0-0.5 mg/L as CaCO3 (Varies)

## Slide 64: Need Alkalinity?
What chemicals can be used to increase alkalinity?
    Lime, CaO or Ca(OH)2
    Soda ash, Na2CO3
    Caustic soda, NaOH
    Sodium bicarbonate, NaHCO3
Lime is least expensive, but can be difficult to handle and feed.
Alkalinity = [OH-1] + [HCO3-1] + 2[CO3-2] – [H+]
Notes: How do each of these increase alkalinity?
Does it matter which chemical you use???!

## Slide 65: Alkalinity increase per addition of 1 mg/L of Alkali
1 mg/l Alkali added
Hydrated lime (95%)
Unslaked Lime(90%)
Caustic Soda
Soda Ash
Increases Alkalinity
1.28 mg/L as CaCO3
1.61 mg/L as CaCO3
1.25 mg/L as CaCO3
0.94 mg/L as CaCO3

## Slide 66: Break

## Slide 67: Test Prep:
Q: As the TOC increases, the TOC percentage removal required from a source water supply _______.
Increases as alkalinity increases
Increases as alkalinity decreases
Decreases as pH increases
Decreases as temperature increases
Water Operator Certification Exam Prep: page 86, #189

## Slide 68: Stage 1 D/DBP Rule:
Required Percent Removal of TOC based on source water TOC and alkalinity |  |  | 
 | Alkalinity |  | 
TOC (mg/L) | 0-60 mg/L | 60-120 mg/L | >120 mg/L
less than 2.0 mg/L | no action | no action | no action
2.0 to <4.0 mg/L | 35 | 25 | 15
4.0 to <8.0 mg/L | 45 | 35 | 25
greater than 8.0 mg/L | 50 | 40 | 30
Notes: As TOC increases, you are moving down the table.
As Alkalinity increases, the required removal of TOC decreases
Or, conversely, as Alkalinity decreases, the required TOC removal increases.

## Slide 69: Test Prep:
Q: As the TOC increases, the TOC percentage removal required from a source water supply _______.
Increases as alkalinity increases
Increases as alkalinity decreases
Decreases as pH increases
Decreases as temperature increases
Answer: b. Increases as alkalinity decreases
Water Operator Certification Exam Prep: page 86, #189

## Slide 70
Jar Tests
Zeta Meter
Streaming Current Monitor
UV254/TOC/Specific Ultraviolet Absorbance
Trends (turbidity, headloss, particle counts)
Coagulation Evaluation Tools
Notes: How do we know we are getting IT right? My favorite are trends, but trends do not tell you everything  which way to go (up or down), or effectiveness of alternate coagulants, polymers, oxidants, etc. And we do not often have time or ability to test every combination on full-scale so we need additional tools.
Tools for evaluating coagulation chemicals and dose

## Slide 71: “Standard” 6 Jar – Tester
Provides visual observation of floc development
Allows for multiple evaluations to be performed simultaneously
Can be used to simulate plant operating characteristics
Notes: Evaluate multiple doses, coagulant aids, pH simultaneously.
Very good idea what your TOC/DOC removal will be for a given coagulant product and dose.
But they have their limitations ….
Not accurate for HM or LH at NNWW

## Slide 72: Jar Tests
Don’t try to do too much!
Jar tests will not accurately predict residual turbidity because flocculation and settling are scale dependent. Rather, focus on trend of turbidity as a function of coagulant dose.
Jar tests do accurately predict DOC and UV254 removals because removal of NOM is a chemical reaction so NOM removal does not depend on separation by clarification or filtration.
Chemistry is independent of scale so the optimum dose and pH in a jar test will also be the optimum for the full-scale plant. (Mixing disclaimer!)
Notes: Filterability Index
Focus on which chemical and how much
Don’t over scrutinize flocculation
Don’t rely on just visual observations alone.

## Slide 73
Zeta potential is the natural repelling electrical force between any two particles of like charge that keep them suspended. (Water Supply Operations)
Most naturally occurring particles have a net negative surface charge
Coagulation reduces or neutralizes the particle charge so particles will aggregate
Notes: Recall: most naturally occurring particles have a net negative surface charge; like charges repel  stable suspension. Do not want to aggregate into larger particles.
Coagulation reduces or neutralizes the particle charges so the particles will aggregate and/or provide positively charged species that will form complexes with NOM and precipitate out.

## Slide 74: Coagulation Evaluation Tools
Zeta Meter
  Effectively measures the repulsive force between colloids  “Zeta Potential”
  Provides immediate results
  Can be used in conjunction with Jar Tests to quickly evaluate coagulant performance

## Slide 75
Zeta Potential
“Electrical Potential Curve” indicates strength of repulsive forces between particles and distance at which they come into play.
Notes: The highly charged surface of the particle and layers of charged ions surrounding the particle create an electrostatic potential between the particle and bulk solution. The potential is greatest at the particle surface and decreases with distance as move away from the particle surface. Electrical Potential curve.
Coagulant addition reduces the negative surface charge of particles by adding positively charged molecules so that the attractive Van der Waals forces can bring the particles together and form larger floc.

## Slide 76: Zeta Potential – Rule of Thumb
Coagulation Level | Avg. ZP in mV
Moderate Stability | -40 to -31
Plateau of Slight Stability | -30 to -21
Threshold of Agglomeration | -20 to -11
Fair Agglomeration | -10 to -5
Excellent Coagulation | -4 to -1
Maximum Coagulation | 0 to +3
Source unknown
Gregory and Carlson reported that a zeta potential between +1 and +4 was optimum for their study (2002)
Notes: And a slightly positive zeta potential has proved to be effective for both surface water plants in Newport News.

## Slide 77: Zeta Potential Operating Range
Notes: According to Malvern Panalytical (June 2020), this data from 30 different river sources.  show optimum operating range of -5 mV to +3 mV.

## Slide 78: Coagulation Evaluation Tools
Zeta Potential
  Do not need to measure zeta potential everyday unless source water quality changing quickly.
  Some degree of variability  Collect enough data to identify trends and outliers.
  Do not make coagulant dose changes based on one data point; look for confirmation and trends.
Notes: Can measure every day to create trends, figure out a plant’s “sweet spot”

## Slide 79
Jar Tests
Zeta Meter
Streaming Current Monitor
UV254/TOC/Specific Ultraviolet Absorbance
Trends (turbidity, headloss, particle counts)
Coagulation Evaluation Tools
Notes: How do we know we are getting IT right? My favorite are trends, but trends do not tell you everything  which way to go (up or down), or effectiveness of alternate coagulants, polymers, oxidants, etc. And we do not often have time or ability to test every combination on full-scale so we need additional tools.
Tools for evaluating coagulation chemicals and dose

## Slide 80: Coagulation Training
Newport News Waterworks
Notes: Need to cull out more slides

## Slide 81: Add coagulant to:
Remove turbidity
Remove natural organic matter
  Measured as Total Organic Carbon (TOC) and/or UV254
  Imparts color
  Oxidant demand
  Precursor disinfection by-products (THMs, HAAs)

## Slide 82: Coagulation Drivers
At Newport News, our reservoir system removes most suspended solids such that raw water turbidity is almost always < 10 NTU.
Total organic carbon (TOC) levels are typically 5-8 mg/L as C. Therefore, TOC drives alum dose.
We practice enhanced coagulation to remove as much DBP precursor material as practical.

## Slide 83: Required Coagulant Dose
Rule of thumb: 10 mg/L of Alum required for every 1 mg/L of TOC.
This is a guideline we use to make sure we are in the ballpark.
We then look at several other factors to determine if an alum dose change is necessary or if raw water quality conditions are changing and might soon require a coagulant dose change.
 Alum dose : TOC ratio will change based on nature of NOM

## Slide 84: Water quality and performance factors considered in Coagulation Assessment
Total organic carbon
Zeta potential measured just after rapid mix
Rapid mix pH
Clarifier alkalinity
Clarifier performance and combined filter effluent turbidity trends
Filter ripening times after backwash
Initial filter turbidity after ripening
Filter turbidity breakthrough during course of filter run

## Slide 85: Coagulation Strategy
 We first look at the latest TOC and Zeta measurements. TOC is measured 1x/week; Zeta is measured at least 3x/week or more frequently if conditions are changing.
Generally, TOC changes seasonally and gradually. However, it may change more quickly following major weather events. In those cases, we will also look at UV-254 as operators monitor it daily and there is a good correlation between UV-254 and TOC.

## Slide 86: Raw water TOC and UV-254 correlation
Chart: LEE HALL WTP 2015
| 42009 | 42016 | 42023 | 42030 | 42037 | 42044 | 42051 | 42058 | 42065 | 42072 | 42079 | 42086 | 42093 | 42100 | 42107 | 42114 | 42121 | 42128 | 42135 | 42142 | 42149 | 42152 | 42157 | 42164 | 42171 | 42178 | 42185 | 42192 | 42199 | 42206 | 42213 | 42220 | 42227 | 42234 | 42241 | 42248 | 42256 | 42261 | 42268 | 42275 | 42282 | 42289 | 42296 | 42303 | 42310 | 42317 | 42324 | 42331 | 42338 | 42345 | 42352 | 42359
Raw TOC MG/L | 5.56 | 5.92 | 5.37 | 5.83 | 5.8 | 5.72 | 5.35 | 5.41 | 5.96 | 5.64 | 5.59 | 5.81 | 5.96 | 5.98 | 5.72 | 5.67 | 5.67 | 6.07 | 6.16 | 5.77 | 6.66 | 7.49 | 7.74 | 7.61 | 7.2 | 7.46 | 7.17 | 7.28 | 6.64 | 6.76 | 7.03 | 7.69 | 7.5 | 7.41 | 6.67 | 6.84 | 6.23 | 6.55 | 5.5 | 6.78 | 6.34 | 9.04 | 8.21 | 9.01 | 8.78 | 7.31 | 8.39 | 7.56 | 7.38 | 7.18 | 6.8
CLW TOC | 3.29 | 3.36 | 3.11 | 3.18 | 3.37 | 3.22 | 3 | 2.97 | 2.86 | 2.84 | 2.85 | 2.99 | 3.25 | 3.47 | 2.91 | 2.8 | 2.62 | 2.72 | 2.85 | 2.81 | 2.94 | 3.1 | 3.06 | 3.48 | 3.4 | 3.19 | 3.18 | 2.96 | 3.29 | 3.39 | 3.4 | 3.5 | 3.31 | 3.09 | 3.23 | 2.92 | 2.98 | 3.23 | 3.04 | 3.44 | 4.27 | 3.74 | 3.6 | 3.91 | 3.65 | 3.88 | 3.54 | 3.35 | 3.4 | 3.48
FE TOC | 2.8 | 2.84 | 2.69 | 2.7 | 2.74 | 2.77 | 2.59 | 2.63 | 2.68 | 2.46 | 2.52 | 2.59 | 2.67 | 2.73 | 2.56 | 2.29 | 2.11 | 2.14 | 2.27 | 2.09 | 2.41 | 2.2 | 2.32 | 2.25 | 2.43 | 2.3 | 1.9 | 2.36 | 2.63 | 2.42 | 2.48 | 2.49 | 2.37 | 2.28 | 2.35 | 2.19 | 2.27 | 2.15 | 2.28 | 2.42 | 2.74 | 2.84 | 3.01 | 3.24 | 3.11 | 3.53 | 3.02 | 2.91 | 2.9 | 2.86
FW TOC | 2.87 | 3.01 | 2.76 | 3.82 | 2.87 | 2.84 | 2.76 | 2.9 | 2.54 | 2.5 | 2.31 | 2.54 | 2.43 | 2.55 | 2.38 | 2.62 | 2.03 | 2.1 | 2.04 | 2.41 | 2.06 | 2.14 | 2.22 | 2.17 | 2.66 | 2.42 | 2.46 | 2.28 | 2.27 | 2.16 | 2.44 | 2.48 | 2.4 | 2.28 | 2.37 | 2.23 | 2.16 | 2.2 | 2.6 | 2.65 | 2.63 | 2.96 | 3.24 | 3.31 | 3.23 | 3.38 | 3.21 | 2.78 | 2.69 | 2.62
Chart: LEE HALL Reservoir
| 5.5 | 5.68 | 5.77 | 5.68 | 5.93 | 5.76 | 5.63 | 5.4 | 5.26 | 5.29 | 5.49 | 5.54 | 5.76 | 6.21 | 5.61 | 5.53 | 5.63 | 5.73 | 6.04 | 5.8 | 6.62 | 7.29 | 7.32 | 7.24 | 7.07 | 6.96 | 6.96 | 6.52 | 6.62 | 6.93 | 7.57 | 7.3 | 7.13 | 6.53 | 6.73 | 5.96 | 5.75 | 5.52 | 6.47 | 6.58 | 7.3 | 7.94 | 7.94 | 8.15 | 7.19 | 7.61 | 7.48 | 7.41 | 7.37 | 6.95 | 6.66
Raw UV254 Filt | 0.144 | 0.147 | 0.162 | 0.147 | 0.161 | 0.154 | 0.141 | 0.155 | 0.143 | 0.152 | 0.153 | 0.177 | 0.182 | 0.178 | 0.172 | 0.163 | 0.174 | 0.178 | 0.166 | 0.158 | 0.209 | 0.221 | 0.257 | 0.226 | 0.208 | 0.21 | 0.2 | 0.186 | 0.189 | 0.213 | 0.232 | 0.243 | 0.213 | 0.188 | 0.19 | 0.129 | 0.152 | 0.142 | 0.158 | 0.201 | 0.235 | 0.247 | 0.246 | 0.244 | 0.234 | 0.245 | 0.214 | 0.244 | 0.257 | 0.232 | 0.224
Focus on dark blue line (RAW water TOC); pink = clarified, red = filtered, light blue = finished
Shows correlation between raw water TOC (DOC) and UV254.

## Slide 87: Trends are accessible from SCADA slides (one-click)
Trend icons

## Slide 92: Storm Event – Early October 2015
Chart: LEE HALL WTP 2015
| 42009 | 42016 | 42023 | 42030 | 42037 | 42044 | 42051 | 42058 | 42065 | 42072 | 42079 | 42086 | 42093 | 42100 | 42107 | 42114 | 42121 | 42128 | 42135 | 42142 | 42149 | 42152 | 42157 | 42164 | 42171 | 42178 | 42185 | 42192 | 42199 | 42206 | 42213 | 42220 | 42227 | 42234 | 42241 | 42248 | 42256 | 42261 | 42268 | 42275 | 42282 | 42289 | 42296 | 42303 | 42310 | 42317 | 42324 | 42331 | 42338 | 42345 | 42352 | 42359
Raw TOC MG/L | 5.56 | 5.92 | 5.37 | 5.83 | 5.8 | 5.72 | 5.35 | 5.41 | 5.96 | 5.64 | 5.59 | 5.81 | 5.96 | 5.98 | 5.72 | 5.67 | 5.67 | 6.07 | 6.16 | 5.77 | 6.66 | 7.49 | 7.74 | 7.61 | 7.2 | 7.46 | 7.17 | 7.28 | 6.64 | 6.76 | 7.03 | 7.69 | 7.5 | 7.41 | 6.67 | 6.84 | 6.23 | 6.55 | 5.5 | 6.78 | 6.34 | 9.04 | 8.21 | 9.01 | 8.78 | 7.31 | 8.39 | 7.56 | 7.38 | 7.18 | 6.8
CLW TOC | 3.29 | 3.36 | 3.11 | 3.18 | 3.37 | 3.22 | 3 | 2.97 | 2.86 | 2.84 | 2.85 | 2.99 | 3.25 | 3.47 | 2.91 | 2.8 | 2.62 | 2.72 | 2.85 | 2.81 | 2.94 | 3.1 | 3.06 | 3.48 | 3.4 | 3.19 | 3.18 | 2.96 | 3.29 | 3.39 | 3.4 | 3.5 | 3.31 | 3.09 | 3.23 | 2.92 | 2.98 | 3.23 | 3.04 | 3.44 | 4.27 | 3.74 | 3.6 | 3.91 | 3.65 | 3.88 | 3.54 | 3.35 | 3.4 | 3.48
FE TOC | 2.8 | 2.84 | 2.69 | 2.7 | 2.74 | 2.77 | 2.59 | 2.63 | 2.68 | 2.46 | 2.52 | 2.59 | 2.67 | 2.73 | 2.56 | 2.29 | 2.11 | 2.14 | 2.27 | 2.09 | 2.41 | 2.2 | 2.32 | 2.25 | 2.43 | 2.3 | 1.9 | 2.36 | 2.63 | 2.42 | 2.48 | 2.49 | 2.37 | 2.28 | 2.35 | 2.19 | 2.27 | 2.15 | 2.28 | 2.42 | 2.74 | 2.84 | 3.01 | 3.24 | 3.11 | 3.53 | 3.02 | 2.91 | 2.9 | 2.86
FW TOC | 2.87 | 3.01 | 2.76 | 3.82 | 2.87 | 2.84 | 2.76 | 2.9 | 2.54 | 2.5 | 2.31 | 2.54 | 2.43 | 2.55 | 2.38 | 2.62 | 2.03 | 2.1 | 2.04 | 2.41 | 2.06 | 2.14 | 2.22 | 2.17 | 2.66 | 2.42 | 2.46 | 2.28 | 2.27 | 2.16 | 2.44 | 2.48 | 2.4 | 2.28 | 2.37 | 2.23 | 2.16 | 2.2 | 2.6 | 2.65 | 2.63 | 2.96 | 3.24 | 3.31 | 3.23 | 3.38 | 3.21 | 2.78 | 2.69 | 2.62
Raw water TOC increased from ~6.5 mg/L to 9 mg/L very quickly
Previous trends show what good performance looks like. Following trends will show how we detect that performance is changing and how plant responds to our coagulant dose changes.

## Slide 95
Last alum dose change appears to have moved us out of the center of our sweet spot. Ripening times still ok, but CFE turbidity and turbidity after backwash not as good.
Notes: Instruments and trends allow us to see very subtle changes in performance that would not be detected on an overview slide!
Balance between plant performance and chemical usage

## Slide 96
Notes: Cannot discern subtle changes or trends from snapshot of filter data!

## Slide 98: Coagulant Change at Harwood’s Mill

## Slide 99: Normal vs Upset

## Slide 100: Zeta Potential Analysis

## Slide 101: Questions?

## Slide 102
Bruce Utne, butne@nnva.gov
John Hanchak Jr., jhanchak@nnva.gov
Newport News Waterworks
Notes: So glad this is not my plant (and I’m not this guy)!